## Summary
Particulars | No. | Total MVAR | [13 empty] | Dharamjaygarh-Ranchi-II@Ranchi-240 SLR
765 240 MVAR BRs | 28 | 6720 |  | 765 kV S/S | 765 kV Lines | 765/400 kV ICTS | 765 kV Line Reactors in WR |  |  |  | 765 kV Bus Reactors in WR |  | Total Reactors & MVAR |  |  | Dharamjaygarh-Ranchi-I@Ranchi-240 SLR
765 330 MVAR BRs | 3 | 990 |  |  |  |  | 240 MVAR |  | 330 MVAR |  | 240 MVAR | 330 MVAR |  |  |  | Gwalior-Jaipur-I@Jaipur 240
765 kV End-1 240 MVAR SLRs | 32 | 7680 |  |  |  |  | S/W | Non S/W | S/W | Non S/W | [5 empty] | Gwalior-Jaipur-II@Jaipur 240
765 kV End-1 240 MVAR NSLRs | 17 | 4080 | No. | 27 | 68 | 53 | 52 | 36 | 10 | 4 | 29 | 3 | 134 |  |  | Solarpur-Raichur-I@Raichur240
765 kV End-1 330 MVAR SLRs | 7 | 2310 | MVAR | - | - | - | 12480 | 8640 | 3300 | 1320 | 6960 | 990 | 33690 |  |  | Solarpur-Raichur-II@Raichur240
765 kV End-1 330 MVAR NSLRs | 3 | 990
765 kV End-2 240 MVAR SLRs | 16 | 3840 |  | 1200 kV S/S | 1200 kV Lines | 1200/400 kV ICTS
765 kV End-2 240 MVAR NSLRs | 24 | 5760
765 kV End-2 330 MVAR SLRs | 2 | 660
765 kV End-2 330 MVAR NSLRs | 2 | 660 | No. | 1 | 1 | 2
| 134 | 33690 | MVAR | - | - | -
Particulars | No. | Total MVAR |  | 400 kV S/S | 400 kV Lines | 400/220 kV ICTS | 400 kV Lines Reactors in WR | [5 empty] | 400 kV Bus Reactors in WR |  |  |  | Total
400 kV 50 MVAR BRs | 35 | 1750 |  |  |  |  | 50 MVAR |  | 63 MVAR |  | 80 MVAR |  | 50 MVAR | 63 MVAR | 80 MVAR | 125 MVAR
400 kV 63 MVAR BRs | 18 | 1134 |  |  |  |  | S/W | Non S/W | S/W | Non S/W | S/W | Non S/W
400 kV 80 MVAR BRs | 28 | 2240 | No. | 156 | 399 | 212 | 12 | 123 | 9 | 38 | 5 | 9 | 36 | 18 | 28 | 43 | 321
400 kV 125 MVAR BRs | 41 | 5125 | MVAR | - | - | - | 600 | 6150 | 567 | 2394 | 400 | 720 | 1800 | 1134 | 2240 | 5375 | 21380
400 kV End-1 50 MVAR SLRs | 3 | 150
400 kV End-1 50 MVAR NSLRs | 63 | 3150
400 kV End-1 63 MVAR SLRs | 7 | 441 |  |  |  |  | Zerda-Binmal @Binmal 50 MVAR
400 kV End-1 63 MVAR NSLRs | 13 | 819
400 kV End-1 80 MVAR SLRs | 2 | 160
400 kV End-1 80 MVAR NSLRs | 5 | 400
400 kV End-2 50 MVAR SLRs | 7 | 350
400 kV End-2 50 MVAR NSLRs | 60 | 3000
400 kV End-2 63 MVAR SLRs | 2 | 126
400 kV End-2 63 MVAR NSLRs | 21 | 1323
400 kV End-2 80 MVAR SLRs | 3 | 240
400 kV End-2 80 MVAR NSLRs | 4 | 320
| 215 | 20728

## Summary 400 kV SS
S.No | S/S | Line Reactors | [5 empty] | Bus Reactors |  |  |  | Total LRs MVAR | Total BRs MVAR | Total S/W MVAR at SS | Total S/S MVAR Resources
|  | 50 MVAR |  | 63 MVAR |  | 80 MVAR |  | 50 MVAR | 63 MVAR | 80 MVAR | 125 MVAR
|  | S/W | Non S/W | S/W | Non S/W | S/W | Non S/W
1 | ACBIL | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2 | Akola | 0 | 2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 100 | 0 | 0 | 100
3 | Akola(2) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
4 | Amreli | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 175 | 175 | 175
5 | APL-Mundra | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 1 | 0 | 285 | 285 | 285
6 | Asoj | 0 | 3 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 150 | 50 | 50 | 200
7 | Astha | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 50 | 50 | 50 | MP
8 | Athena | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
9 | Aurangabad-M(Waluj) | 0 | 3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 150 | 0 | 0 | 150
10 | Aurangabad-PG | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 0 | 0 | 1 | 260 | 125 | 285 | 385
11 | Bableshwar | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 0 | 0 | 160 | 160 | 160 |  | 6480
12 | Bachau | 0 | 0 | 0 | 2 | 0 | 0 | 0 | 1 | 0 | 1 | 126 | 188 | 188 | 314 |  | 3314
13 | Balco | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
14 | Bhadrawati | 0 | 4 | 0 | 4 | 0 | 0 | 1 | 0 | 0 | 0 | 452 | 50 | 50 | 502
15 | Bhatapara | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 50 | 125 | 125 | 175
16 | Bhilai | 0 | 5 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 330 | 0 | 0 | 330 | MP
17 | Bhopal-BDTCL | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 125 | 125 | 125 | MP
18 | Bhopal-MP | 0 | 2 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 100 | 205 | 205 | 305
19 | Bhusawal (Khadka) | 0 | 2 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 100 | 50 | 50 | 150
20 | Bilaspur | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | MP
21 | Bina-MP | 0 | 2 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 100 | 50 | 50 | 150 | MP
22 | Bina-NHPTL | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
23 | Bina-NTS | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | MP
24 | Bina-PG | 0 | 4 | 2 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 326 | 125 | 251 | 451
25 | Birsingpur | 0 | 1 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 0 | 113 | 50 | 50 | 163
26 | Boisar | 0 | 0 | 0 | 0 | 0 | 2 | 0 | 0 | 0 | 0 | 160 | 0 | 0 | 160
27 | CGPL | 0 | 0 | 4 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 252 | 63 | 315 | 315
28 | Chakan | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
29 | Champa | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 80 | 80 | 80 | MP
30 | Chandrapur | 0 | 3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 150 | 0 | 0 | 150
31 | Chandrapur-II | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | MP
32 | Chhegaon | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 50 | 50 | 50
33 | Chorania | 0 | 2 | 0 | 2 | 0 | 0 | 1 | 0 | 0 | 1 | 226 | 175 | 175 | 401
34 | Damoh | 0 | 3 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 1 | 150 | 188 | 188 | 338
35 | DB-Power | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
36 | Deepnagar | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
37 | Dehgam | 0 | 2 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 1 | 100 | 188 | 188 | 288
38 | DGEN | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 125 | 125 | 125
39 | Dhariwal | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 80 | 80 | 80
40 | Dhariwal-MS | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 80 | 80 | 80
41 | Dhule-BDTCL | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
42 | Dhule-MS | 2 | 2 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 200 | 80 | 180 | 280
43 | EMCO | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 80 | 80 | 80
44 | Essar_Mahan | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 80 | 80 | 80
45 | Gandhar | 0 | 1 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 50 | 50 | 50 | 100 | MP
46 | GMR-CG | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 125 | 125 | 125
47 | GPEC | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
48 | Gwalior | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3 | 0 | 375 | 375 | 375
49 | Hadala | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 63 | 175 | 175 | 238 | MP
50 | Hazira | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | MP
51 | IEPL | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | MP
52 | Indira Sagar | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | MP
53 | Indore-MP | 0 | 5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 250 | 0 | 0 | 250 | MP
54 | Indore-PG | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 1 | 0 | 188 | 188 | 188 | MP
55 | Itarsi | 1 | 7 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 2 | 400 | 300 | 350 | 700
56 | Jabalpur | 2 | 2 | 0 | 4 | 0 | 0 | 0 | 1 | 0 | 1 | 452 | 188 | 288 | 640
57 | Jabalpur (PS) | 0 | 2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 100 | 250 | 250 | 350
58 | Jaigad | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 0 | 0 | 0 | 0 | 100 | 100 | 100 | MP
59 | Jejuri | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | MP
60 | Jetpur | 0 | 0 | 0 | 2 | 0 | 0 | 1 | 1 | 0 | 0 | 126 | 113 | 113 | 239
61 | Jhabua Power | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
62 | JP-Bina | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | MP
63 | JPL | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 125 | 125 | 125 | MP
64 | JPL_extn(Tamnar) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
65 | JP-Nigrie | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 125 | 125 | 125
66 | Julwania | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 50 | 50 | 50
67 | Kala | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 80 | 80 | 80
68 | Kalwa | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | MP
69 | Karad | 0 | 1 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 130 | 80 | 80 | 210 | MP
70 | Kasor | 0 | 2 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 100 | 175 | 175 | 275
71 | Katni | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
72 | Khandwa | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 0 | 0 | 2 | 260 | 250 | 410 | 510
73 | Khaparkheda | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
74 | Kharghar | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 80 | 80 | 80
75 | Kolhapur | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 80 | 80 | 80
76 | Kolhapur-PG | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 125 | 125 | 125
77 | Koradi | 0 | 2 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 100 | 50 | 50 | 150
78 | Koradi-II | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
79 | Korba (W) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
80 | Korba (W)-Ext | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
81 | Korba-NTPC | 0 | 2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 100 | 0 | 0 | 100
82 | Kosamba | 0 | 0 | 0 | 2 | 0 | 0 | 0 | 0 | 1 | 0 | 126 | 80 | 80 | 206
83 | Koyna stage-IV | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
84 | KSK Mahanadi | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
85 | KWPCL | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
86 | Lara | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | MP
87 | Lonikhand | 0 | 1 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 50 | 50 | 50 | 100
88 | Lonikhand-II | 0 | 2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 100 | 0 | 0 | 100
89 | Magarawada | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 80 | 80 | 80
90 | Malwa | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | MP
91 | Mansar | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 63 | 63 | 63
92 | Mapusa | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 50 | 50 | 50
93 | Marwa | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | MP
94 | MB Power | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 125 | 125 | 125
95 | MCCPL | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
96 | Mouda | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 80 | 80 | 80
97 | Nagda | 0 | 4 | 0 | 0 | 0 | 0 | 2 | 0 | 0 | 0 | 200 | 100 | 100 | 300
98 | Nagothane | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 80 | 80 | 80
99 | Nanded | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
100 | Nandgaonpeth | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 80 | 80 | 80
101 | Navsari | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 63 | 63 | 63
102 | New koyna | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
103 | NSPCL | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
104 | Padghe | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 50 | 80 | 80 | 130
105 | Parli-M | 0 | 6 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 300 | 50 | 50 | 350 | MP
106 | Parli-PG | 0 | 2 | 0 | 4 | 0 | 0 | 0 | 1 | 0 | 1 | 352 | 188 | 188 | 540
107 | Pathadi | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
108 | Pirana-PG | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 125 | 125 | 125
109 | Pirana-T | 0 | 2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 100 | 0 | 0 | 100
110 | Pithampur | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 50 | 50 | 50
111 | Pune-PG | 4 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 200 | 50 | 250 | 250
112 | Pune-PG(Shikrapur) | 2 | 2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 200 | 0 | 100 | 200
113 | Raigarh | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 1 | 0 | 188 | 188 | 188 | MP
114 | Raigarh-PS(Kotra) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 80 | 80 | 80
115 | Raipur | 1 | 4 | 0 | 7 | 0 | 1 | 0 | 0 | 1 | 1 | 771 | 205 | 255 | 976
116 | Raipur-PS(Durg) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
117 | Raita | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
118 | Rajgarh | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 125 | 125 | 125 | MP
119 | Ranchodpura | 0 | 2 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 100 | 175 | 175 | 275 | MP
120 | RGPPL | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | MP
121 | RKM | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 0 | 0 | 0 | 0 | 100 | 100 | 100 | MP
122 | Sami | 0 | 2 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 100 | 50 | 50 | 150
123 | Sasan | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 50 | 0 | 0 | 50 | MP
124 | Satna | 0 | 8 | 0 | 0 | 0 | 0 | 1 | 1 | 0 | 0 | 400 | 113 | 113 | 513
125 | Satpura | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 2 | 0 | 0 | 50 | 126 | 126 | 176
126 | Seoni | 0 | 1 | 0 | 0 | 0 | 2 | 0 | 0 | 0 | 2 | 210 | 250 | 250 | 460
127 | Sholapur-M | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
128 | Shujalpur | 0 | 4 | 2 | 0 | 0 | 0 | 0 | 1 | 0 | 1 | 326 | 188 | 314 | 514
129 | Sipat | 0 | 0 | 0 | 0 | 0 | 2 | 0 | 0 | 0 | 0 | 160 | 0 | 0 | 160
130 | SKS | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 50 | 50 | 50
131 | Soja | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 1 | 0 | 0 | 130 | 130 | 130
132 | Solapur-NTPC | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
133 | Solapur-PG | 0 | 2 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 180 | 63 | 143 | 243
134 | SSP | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
135 | Sugen | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
136 | Tamnar | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
137 | Taptithanda | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
138 | Tarapur-3&4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
139 | Tiroda | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 0 | 0 | 160 | 160 | 160
140 | TRN | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
141 | Ukai | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
142 | Uno-Sugen | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 80 | 80 | 80
143 | Vadinar | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | MP
144 | Vadodara-PS | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | MP
145 | Vandana | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 50 | 0 | 0 | 50 | MP
146 | Vapi | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | MP
147 | Varsana | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 175 | 175 | 175 | MP
148 | Vindhyachal | 0 | 6 | 1 | 3 | 0 | 0 | 1 | 1 | 0 | 0 | 552 | 113 | 176 | 665
149 | Vindhyachal-III | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
150 | Vindhyachal-IV | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 80 | 80 | 80
151 | Vindhyachal-PS | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 125 | 125 | 125
152 | Vindhyachal-V | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 63 | 63 | 63
153 | Wanakbori | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
154 | Wardha | 0 | 0 | 0 | 4 | 0 | 0 | 1 | 0 | 0 | 0 | 252 | 50 | 50 | 302
155 | Warora | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 125 | 125 | 125
156 | Zerda(Kansari) | 0 | 2 | 0 | 2 | 0 | 0 | 1 | 0 | 0 | 1 | 226 | 175 | 175 | 401
|  | 12 | 123 | 9 | 38 | 5 | 9 | 36 | 18 | 28 | 43 | 10831 | 10549 | 12116 | 21380

## Summary 765 kV SS
S.No | S/S | Line Reactors |  |  |  | Bus Reactors |  | Total LRs MVAR | Total BRs MVAR | Total S/W MVAR at S/S | Total S/S MVAR Resources
|  | 240 MVAR |  | 330 MVAR |  | 240 MVAR | 330 MVAR
|  | S/W | Non S/W | S/W | Non S/W
1 | Akola(2) | 2 | 2 | 0 | 0 | 1 | 0 | 960 | 240 | 720 | 1200 |  | 240 | 1
2 | Aurangabad-PG | 2 | 4 | 0 | 0 | 1 | 0 | 1440 | 240 | 720 | 1680 |  | 480 | 2
3 | Bhopal-BDTCL | 1 | 1 | 0 | 0 | 1 | 0 | 480 | 240 | 480 | 720 | MP | 240 | 1
4 | Bilaspur | 3 | 0 | 0 | 0 | 1 | 0 | 720 | 240 | 960 | 960 |  | 240 | 1
5 | Bina-NHPTL | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
6 | Bina-PG | 2 | 8 | 0 | 0 | 2 | 0 | 2400 | 480 | 960 | 2880 | MP | 480 | 2
7 | Champa | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 240 | 240 | 240 |  | 240 | 1
8 | Dharamjaygarh | 0 | 1 | 6 | 2 | 0 | 2 | 2880 | 660 | 2640 | 3540 |  | 660
9 | Dhule-BDTCL | 2 | 0 | 0 | 0 | 1 | 0 | 480 | 240 | 720 | 720 |  | 240 | 1
10 | Ektuni (Aurangabad(3)) | 0 | 2 | 0 | 0 | 1 | 0 | 480 | 240 | 240 | 720 | MP | -
11 | Gwalior | 5 | 2 | 0 | 0 | 1 | 0 | 1680 | 240 | 1440 | 1920 | MP | 240 | 1
12 | Indore-PG | 1 | 2 | 0 | 0 | 2 | 0 | 720 | 480 | 720 | 1200 | MP | 480 | 2
13 | Jabalpur-PS | 4 | 4 | 0 | 0 | 2 | 0 | 1920 | 480 | 1440 | 2400 |  | 480 | 2
14 | Koradi(III) | 4 | 0 | 0 | 0 | 1 | 0 | 960 | 240 | 1200 | 1200 |  | 240 | 1
15 | Pune-PG(Shikrapur) | 1 | 0 | 0 | 0 | 1 | 0 | 240 | 240 | 480 | 480 |  | 240 | 1
16 | Raigarh-PS(Kotra) | 2 | 0 | 0 | 0 | 1 | 0 | 480 | 240 | 720 | 720 |  | 240 | 1
17 | Raipur-PS(Durg) | 3 | 2 | 0 | 0 | 1 | 0 | 1200 | 240 | 960 | 1440 | MP | 240 | 1
18 | Sasan | 2 | 0 | 0 | 0 | 1 | 0 | 480 | 240 | 720 | 720 | MP | 240 | 1
19 | Satna | 4 | 4 | 0 | 0 | 2 | 0 | 1920 | 480 | 1440 | 2400 | MP | 480 | 2
20 | Seoni | 3 | 2 | 0 | 0 | 1 | 0 | 1200 | 240 | 960 | 1440 | MP | 240 | 1
21 | Sipat | 2 | 0 | 0 | 0 | 1 | 0 | 480 | 240 | 720 | 720 |  | 240 | 1
22 | Solapur | 5 | 0 | 0 | 0 | 1 | 0 | 1200 | 240 | 1440 | 1440 |  | 240 | 1
23 | Tamnar | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 240 | 240 | 240 |  | 240 | 1
24 | Tiroda | 2 | 0 | 0 | 0 | 1 | 0 | 480 | 240 | 720 | 720 |  | 240 | 1
25 | Vadodora-PS | 0 | 2 | 0 | 0 | 1 | 0 | 480 | 240 | 240 | 720 |  | 240 | 1
26 | Vindhyachal-PS | 2 | 0 | 0 | 0 | 1 | 0 | 480 | 240 | 720 | 720 | MP | 240 | 1
27 | Wardha | 0 | 0 | 4 | 2 | 1 | 1 | 1980 | 570 | 1890 | 2550 |  | 570 | 1
| Total | 52 | 36 | 10 | 4 | 29 | 3 | 25740 | 7950 | 23730 | 33690

## 765kV Lines
Sl No | End-1 | End-2 | Id | Line Owner | End-1 Owner | End-2 Owner | Km | Conductor Type | SIL | No Load MVAR Generated | End1 LR |  | End2 LR |  | End 1 Over Voltage Stage 1 | End 1 Over Voltage Stage 2 | End 2 Over Voltage Stage 1 | End 2 Over Voltage Stage 2 | [5 empty] | End-1 |  |  |  | End-2
[11 empty] | MVAR | S/W | MVAR | S/W | [9 empty] | 240 MVAR SLR | 240 MVAR NSLR | 330 MVAR SLR | 330 MVAR NSLR | 240 MVAR SLR | 240 MVAR NSLR | 330 MVAR SLR | 330 MVAR NSLR
1 | Akola(2) | Ektuni (Aurangabad(3)) | 2 | MEGPTCL | MEGPTCL | MSETCL | 219 | Quad Bersimis | 2194.4416 | 514.65 | 240 | Yes | 240 | - | 110 %-5 Sec | 150 %-0.15 Sec | 110 %-10 Sec | 150 %-0.1 Sec |  | X | B | Zpu | Z(ohms) | 1 | 0 | 0 | 0 | 0 | 1 | 0 | 0
2 | Akola(2) | Ektuni (Aurangabad(3)) | 1 | MEGPTCL | MEGPTCL | WRTS-1 | 219 | Quad Bersimis | 2194.4416 | 514.65 | 240 | Yes | 240 | - | 110 %-7 Sec | 150 %-0.1 Sec | 110 %-8 Sec | 150 %-0.1 Sec | Quad Bersimis | 4.88e-05 | 0.0235 | 0.04557 | 266.6852 | 1 | 0 | 0 | 0 | 0 | 1 | 0 | 0
3 | Aurangabad-PG | Wardha | 1 | WRTS-1 | WRTS-1 | WRTS-1 | 348 | Hexa Zebra | 2470.0035 | 925.68 | 240 | - | 330 | Yes | - | - | - | - | [5 empty] | 0 | 1 | 0 | 0 | 0 | 0 | 1 | 0
4 | Aurangabad-PG | Wardha | 2 | WRTS-1 | WRTS-1 | WRTS-1 | 348 | Hexa Zebra | 2470.0035 | 925.68 | 240 | - | 330 | Yes | - | - | - | - | [5 empty] | 0 | 1 | 0 | 0 | 0 | 0 | 1 | 0
5 | Aurangabad-PG | Wardha | 3 | WRTS-1 | WRTS-1 | WRTS-1 | 370 | Hexa Zebra | 2470.0035 | 984.2 | 240 | - | 330 | Yes | 107 % -5 Sec | 150 %-0.1 Sec | 109 %-5 Sec | 150 %-0.1 Sec | Hexa Zebra | 4.36e-05 | 0.0266 | 0.040486 | 236.9329 | 0 | 1 | 0 | 0 | 0 | 0 | 1 | 0
6 | Aurangabad-PG | Wardha | 4 | WRTS-1 | WRTS-1 | WRTS-1 | 370 | Hexa Zebra | 2470.0035 | 984.2 | 240 | - | 330 | Yes | 107 % -6 Sec | 150 %-0.1 Sec | 109 %-6 Sec | 150 %-0.1 Sec | [5 empty] | 0 | 1 | 0 | 0 | 0 | 0 | 1 | 0
7 | Aurangabad-PG | Solapur-PG | 1 | WRTS-1 | WRTS-1 | WRTS-1 | 279 | Hexa Zebra | 2470.0035 | 742.14 | 240 | Yes | 240 | Yes | 108 % -7 Sec | 150 %-0.1 Sec | 109 %-7 Sec | 150 %-0.1 Sec | [5 empty] | 1 | 0 | 0 | 0 | 1 | 0 | 0 | 0
8 | Aurangabad-PG | Solapur-PG | 2 | WRTS-1 | WRTS-1 | WRTS-1 | 279 | Hexa Zebra | 2470.0035 | 742.14 | 240 | Yes | 240 | Yes | 108 % -8 Sec | 150 %-0.1 Sec | 109 %-8 Sec | 150 %-0.1 Sec | [5 empty] | 1 | 0 | 0 | 0 | 1 | 0 | 0 | 0
9 | Bhopal-BDTCL | Indore-PG | 1 | BDTCL | BDTCL | WRTS-2 | 176 | Quad Bersimis | 2194.4416 | 413.6 | 240 | Yes | 240 | - | 108 % -5 Sec | 150 %-0.1 Sec | 108 % -5 Sec | 150 %-0.1 Sec | [5 empty] | 1 | 0 | 0 | 0 | 0 | 1 | 0 | 0
10 | Bilaspur | Seoni | 1 | WRTS-1 | WRTS-1 | WRTS-1 | 333 | Quad Bersimis | 2194.4416 | 782.55 | 240 | Yes | 240 | - | 108 % -7 Sec | 150 %-0.1 Sec | 108 % -7 Sec | 150 %-0.1 Sec | [5 empty] | 1 | 0 | 0 | 0 | 0 | 1 | 0 | 0
11 | Bilaspur | Seoni | 2 | WRTS-1 | WRTS-1 | WRTS-1 | 335 | Quad Bersimis | 2194.4416 | 787.25 | 240 | Yes | 240 | - | 110 % -5 Sec | 140 %-0.1 Sec | 107 % -5 Sec | 150 %-0.1 Sec | [5 empty] | 1 | 0 | 0 | 0 | 0 | 1 | 0 | 0
12 | Bilaspur | Dharamjaygarh | 1 | WRTS-1 | WRTS-1 | WRTS-1 | 89 | Quad Bersimis | 2194.4416 | 209.15 | 240 | Yes | - | - | 108 %-5 Sec | 150 %-0.1 Sec | 108 %-5 Sec | 150 %-0.1 Sec | [5 empty] | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0
13 | Bina-PG | Gwalior | 1 | WRTS-2 | WRTS-2 | WRTS-2 | 235 | Quad Bersimis | 2194.4416 | 552.25 | 240 | - | 240 | Yes | 108 %-7 Sec | 150 %-0.1 Sec | 108 %-7 Sec | 150 %-0.1 Sec | [5 empty] | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 0
14 | Bina-PG | Jabalpur-PS | 3 | JTCL | WRTS-2 | WRTS-2 | 236 | Quad Bersimis | 2194.4416 | 554.6 | 240 | - | 240 | Yes | 109 %-5 Sec | 150 %-0.1 Sec | 108 %-5 Sec | 150%-0.1 Sec | [5 empty] | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 0
15 | Bina-PG | Gwalior | 2 | WRTS-2 | WRTS-2 | WRTS-2 | 235 | Quad Bersimis | 2194.4416 | 552.25 | 240 | - | 240 | Yes | 108 %-7 Sec | 150 %-0.1 Sec | 108 %-7 Sec | 150 %-0.1 Sec | [5 empty] | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 0
16 | Bina-PG | Gwalior | 3 | WRTS-2 | WRTS-2 | WRTS-2 | 231 | Quad Bersimis | 2194.4416 | 542.85 | 240 | Yes | 240 | Yes | 108 %-5 Sec | 150 %-0.1 Sec | 108 %-5 Sec | 150 %-0.1 Sec | [5 empty] | 1 | 0 | 0 | 0 | 1 | 0 | 0 | 0
17 | Bina-PG | Indore-PG | 1 | WRTS-2 | WRTS-2 | WRTS-2 | 310 | Quad Bersimis | 2194.4416 | 728.5 | 240 | Yes | 240 | - | 109 %-8 Sec | 150 %-0.1 Sec | 109 %-8 Sec | 150 %-0.1 Sec | [5 empty] | 1 | 0 | 0 | 0 | 0 | 1 | 0 | 0
18 | Bina-PG | Jabalpur-PS | 1 | WRTS-2 | WRTS-2 | WRTS-2 | 230 | Quad Bersimis | 2194.4416 | 540.5 | 240 | - | 240 | Yes | 109 %-5 Sec | 150 %-0.1 Sec | 109 %-5 Sec | 150 %-0.1 Sec | [5 empty] | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 0
19 | Bina-PG | Jabalpur-PS | 2 | WRTS-2 | WRTS-2 | WRTS-2 | 230 | Quad Bersimis | 2194.4416 | 540.5 | 240 | - | 240 | Yes | 108 %- 5 Sec | 150 %-0.1 Sec | 108 %- 5 Sec | 150 %-0.1 Sec | [5 empty] | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 0
20 | Bina-PG | Bina-NHPTL | 1 | WRTS-2 | WRTS-2 | NHPTL | 0.2 | Quad Bersimis | 2194.4416 | 0.47 | - | - | - | - | [9 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
21 | Dharamjaygarh | Ranchi | 1 | ERTS-1/WRTS-1 | WRTS-1 | ERTS-1 | 301 | Quad Bersimis | 2194.4416 | 707.35 | 330 | - | 240 | Yes | 107 % -5 Sec | 150 %-0.1 Sec | 107 % -5 Sec | 150 %-0.1 Sec | [5 empty] | 0 | 0 | 0 | 1 | 1 | 0 | 0 | 0
22 | Dharamjaygarh | Ranchi | 2 | ERTS-1/WRTS-1 | WRTS-1 | ERTS-1 | 303 | Quad Bersimis | 2194.4416 | 712.05 | 330 | - | 240 | Yes | 108 %-7 Sec | 150 %-0.1 Sec | 108 %-7 Sec | 150 %-0.1 Sec | [5 empty] | 0 | 0 | 0 | 1 | 1 | 0 | 0 | 0
23 | Dharamjaygarh | Raipur-PS(Durg) | 2 | WRTS-1 | WRTS-1 | WRTS-1 | 200 | Quad Bersimis | 2194.4416 | 470 | 240 | - | - | - | 108 %-5 Sec | 150%-0.1 Sec | ERLDC | ERLDC | [5 empty] | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0
24 | Dharamjaygarh | Jharsuguda | 1 | WRTS-2 | WRTS-2 | ERTS-2 | 303 | Hexa Zebra | 2470.0035 | 805.98 | 330 | Yes | - | - | 108 %-7 Sec | 150%-0.1 Sec | ERLDC | ERLDC | [5 empty] | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0
25 | Dharamjaygarh | Jharsuguda | 2 | WRTS-2 | WRTS-2 | ERTS-2 | 303 | Hexa Zebra | 2470.0035 | 805.98 | 330 | Yes | - | - | 107 %-5 Sec | 150%-0.1 Sec | 107%-7 Sec | 150 %-0.1 Sec | [5 empty] | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0
26 | Dharamjaygarh | Jabalpur-PS | 1 | WRTS-1 | WRTS-1 | WRTS-2 | 424 | Hexa Zebra | 2470.0035 | 1127.84 | 330 | Yes | 240 | - | 108 %-5 Sec | 150%-0.1 Sec | ERLDC | ERLDC | [5 empty] | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0
27 | Dharamjaygarh | Jabalpur-PS | 2 | WRTS-1 | WRTS-1 | WRTS-2 | 424 | Hexa Zebra | 2470.0035 | 1127.84 | 330 | Yes | 240 | - | 108 %-7 Sec | 150%-0.1 Sec | ERLDC | ERLDC | [5 empty] | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0
28 | Dharamjaygarh | Jabalpur-PS | 3 | JTCL | WRTS-1 | WRTS-2 | 379 | Hexa Zebra | 2470.0035 | 1008.14 | 330 | Yes | 240 | - | 107 %-5 Sec | 150%-0.1 Sec | 108 %- 4 Sec | 150 %-0.1 Sec | [5 empty] | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0
29 | Dharamjaygarh | Jabalpur-PS | 4 | JTCL | WRTS-1 | WRTS-2 | 379 | Hexa Zebra | 2470.0035 | 1008.14 | 330 | Yes | 240 | - | 107 %-7 Sec | 150%-0.1 Sec | 108 %- 5 Sec | 150 %-0.1 Sec | [5 empty] | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0
30 | Dhule-BDTCL | Aurangabad-PG | 1 | BDTCL | BDTCL | WRTS-I | 192 | Quad Bersimis | 2194.4416 | 451.2 | 240 | Yes | - | - | 108 %-5 Sec | 150%-0.1 Sec | 108 %- 6 Sec | 150 %-0.1 Sec | [5 empty] | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0
31 | Gwalior | Agra | 1 | NRTS-1/WRTS-2 | WRTS-2 | NRTS-1 | 129 | Quad Bersimis | 2194.4416 | 303.15 | - | - | - | - | 108 %-7 Sec | 150%-0.1 Sec | 108 %- 7 Sec | 150 %-0.1 Sec | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
32 | Gwalior | Agra | 2 | NRTS-1/WRTS-2 | WRTS-2 | NRTS-1 | 128 | Quad Bersimis | 2194.4416 | 300.8 | - | - | - | - | 110 %-5 Sec | 140 %-0.1 Sec | 108 %-5 Sec | 150 %-0.1 Sec | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
33 | Gwalior | Jaipur | 1 | NRTS-1/WRTS-2 | WRTS-2 | NRTS-1 | 304 | Quad Bersimis | 2194.4416 | 714.4 | 240 | Yes | 240 | - | 108 %-5 Sec | 150 %-0.1 Sec | 108 %-5 Sec | 150 %-0.1 Sec | [5 empty] | 1 | 0 | 0 | 0 | 0 | 1 | 0 | 0
34 | Gwalior | Jaipur | 2 | NRTS-1/WRTS-2 | WRTS-2 | NRTS-1 | 311 | Quad Bersimis | 2194.4416 | 730.85 | 240 | Yes | 240 | - | 109 %-7 Sec | 150 %-0.1 Sec | 109 %-7 Sec | 150 %-0.1 Sec | [5 empty] | 1 | 0 | 0 | 0 | 0 | 1 | 0 | 0
35 | Jabalpur-PS | Bhopal-BDTCL | 1 | BDTCL | WRTS-2 | BDTCL | 260 | Quad Bersimis | 2194.4416 | 611 | 240 | Yes | 240 | - | 108 %-5 Sec | 150 %-0.1 Sec | NRLDC | NRLDC | [5 empty] | 1 | 0 | 0 | 0 | 0 | 1 | 0 | 0
36 | Kholpaur-PG* | Kudgi* | 1 | WRTS-1 | WRTS-1 | SRTS-1 | 191 | Hexa Zebra | 2470.0035 | 508.06 | - | - | - | - | 107 %-4 Sec | 150 %-0.1 Sec | NRLDC | NRLDC | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
37 | Kholpaur-PG* | Kudgi* | 2 | WRTS-1 | WRTS-1 | SRTS-1 | 191 | Hexa Zebra | 2470.0035 | 508.06 | - | - | - | - | 108 %-5 Sec | 150 %-0.1 Sec | 110 %-5 Sec | 150 %-0.1 Sec | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
38 | Koradi(III) | Akola(2) | 1 | MEGPTCL | MEGPTCL | MEGPTCL | 222 | Quad Bersimis | 2194.4416 | 521.7 | 240 | Yes | 240 | - | 110 %-5 Sec | 150 %-0.1 Sec | 110 %-5 Sec | 150 %-0.1 Sec | [5 empty] | 1 | 0 | 0 | 0 | 0 | 1 | 0 | 0
39 | Koradi(III) | Akola(2) | 2 | MEGPTCL | MEGPTCL | MEGPTCL | 222 | Quad Bersimis | 2194.4416 | 521.7 | 240 | Yes | 240 | - | 110 %-7 Sec | 150 %-0.1 Sec | 110 %-7 Sec | 150 %-0.1 Sec | [5 empty] | 1 | 0 | 0 | 0 | 0 | 1 | 0 | 0
40 | Pune-PG(Shikrapur) | Solapur-PG | 1 | WRTS-1 | WRTS-1 | WRTS-1 | 270 | Quad Bersimis | 2194.4416 | 634.5 | 240 | Yes | 240 | Yes | 110 %-7 Sec | 140 %-0.15 Sec | 110 %-7 Sec | 140 %-0.15 Sec | [5 empty] | 1 | 0 | 0 | 0 | 1 | 0 | 0 | 0
41 | Raigarh-PS(Kotra) | Raipur-PS(Durg) | 1 | WRTS-1 | WRTS-1 | WRTS-1 | 235 | Hexa Zebra | 2470.0035 | 625.1 | 240 | Yes | 240 | - | 110 %-5 Sec | 140 %-0.15 Sec | 110 %-5 Sec | 140 %-0.15 Sec | [5 empty] | 1 | 0 | 0 | 0 | 0 | 1 | 0 | 0
42 | Raigarh-PS(Kotra) | Raipur-PS(Durg) | 2 | WRTS-1 | WRTS-1 | WRTS-1 | 235 | Hexa Zebra | 2470.0035 | 625.1 | 240 | Yes | 240 | - | 107 % -5 Sec | 150 %-0.1 Sec | 107 % -5 Sec | 150 %-0.1 Sec | [5 empty] | 1 | 0 | 0 | 0 | 0 | 1 | 0 | 0
43 | Raigarh-PS(Kotra) | Tamnar | 1 | WRTS-1 | WRTS-1 | WRTS-1 | 48 | Hexa Zebra | 2470.0035 | 127.68 | - | - | - | - | 108 %-5 Sec | 150 %-0.1 Sec | 108 %-5 Sec | 150 %-0.1 Sec | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
44 | Raigarh-PS(Kotra) | Tamnar | 2 | WRTS-1 | WRTS-1 | WRTS-1 | 48 | Hexa Zebra | 2470.0035 | 127.68 | - | - | - | - | 107 %-7 Sec | 150 %-0.1 Sec | 107 %-7 Sec | 150 %-0.1 Sec | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
45 | Raigarh-PS(Kotra) | Champa | 1 | WRTS-1 | WRTS-1 | WRTS-1 | 96 | Quad Bersimis | 2194.4416 | 225.6 | - | - | - | - | 108 %-5Sec | 150 %-0.1 Sec | 109 %-5Sec | 150 %-0.1 Sec | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
46 | Raipur-PS(Durg) | Champa | 1 | WRTS-1 | WRTS-1 | WRTS-1 | 153 | Quad Bersimis | 2194.4416 | 359.55 | 240 | Yes | - | - | 109 %-6 Sec | 150 %-0.1 Sec | 109 %-7 Sec | 150 %-0.1 Sec | [5 empty] | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0
47 | Sasan | Satna | 1 | WRTS-2 | SPL | WRTS-2 | 246 | Quad Bersimis | 2194.4416 | 578.1 | 240 | Yes | 240 | - | 108 %-5Sec | 150 %-0.1 Sec | 108 %-5 Sec | 150 %-0.1 Sec | [5 empty] | 1 | 0 | 0 | 0 | 0 | 1 | 0 | 0
48 | Sasan | Satna | 2 | WRTS-2 | SPL | WRTS-2 | 243 | Quad Bersimis | 2194.4416 | 571.05 | 240 | Yes | 240 | - | 109 %-8 Sec | 150 %-0.1 Sec | 108 %-5 Sec | 150 %-0.1 Sec | [5 empty] | 1 | 0 | 0 | 0 | 0 | 1 | 0 | 0
49 | Sasan | Vindhyachal-PS | 1 | WRTS-2 | WRTS-2 | WRTS-2 | 6 | Quad Bersimis | 2194.4416 | 14.1 | - | - | - | - | 110 %-5 Sec | 150 %-0.1 Sec | 109 %-5 Sec | 150 %-0.1 Sec | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
50 | Satna | Gwalior | 1 | WRTS-2 | WRTS-2 | WRTS-2 | 337 | Quad Bersimis | 2194.4416 | 791.95 | 240 | Yes | 240 | - | 110 %-7 Sec | 150 %-0.1 Sec | 108 %-7 Sec | 150 %-0.1 Sec | [5 empty] | 1 | 0 | 0 | 0 | 0 | 1 | 0 | 0
51 | Satna | Gwalior | 2 | WRTS-2 | WRTS-2 | WRTS-2 | 337 | Quad Bersimis | 2194.4416 | 791.95 | 240 | Yes | 240 | - | 107 %-5 Sec | 150 %-0.1 Sec | 110 %-5 Sec | 150 %-0.1 Sec | [5 empty] | 1 | 0 | 0 | 0 | 0 | 1 | 0 | 0
52 | Satna | Bina-PG | 1 | WRTS-2 | WRTS-2 | WRTS-2 | 274 | Quad Bersimis | 2194.4416 | 643.9 | 240 | Yes | 240 | - | 109 %-5 Sec | 150 %-0.1 Sec | 109 %-5 Sec | 150 %-0.1 Sec | [5 empty] | 1 | 0 | 0 | 0 | 0 | 1 | 0 | 0
53 | Satna | Bina-PG | 2 | WRTS-2 | WRTS-2 | WRTS-2 | 276 | Quad Bersimis | 2194.4416 | 648.6 | 240 | Yes | 240 | - | 109 %-6 Sec | 150 %-0.1 Sec | 109 %-6 Sec | 150 %-0.1 Sec | [5 empty] | 1 | 0 | 0 | 0 | 0 | 1 | 0 | 0
54 | Satna | Vindhyachal-PS | 1 | WRTS-2 | WRTS-2 | WRTS-2 | 237 | Quad Bersimis | 2194.4416 | 556.95 | 240 | - | 240 | Yes | 108 %-5 Sec | 150 %-0.1 Sec | 108 %-5 Sec | 150 %-0.1 Sec | [5 empty] | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 0
55 | Satna | Vindhyachal-PS | 2 | WRTS-2 | WRTS-2 | WRTS-2 | 237 | Quad Bersimis | 2194.4416 | 556.95 | 240 | - | 240 | Yes | 109 %-7 Sec | 150 %-0.1 Sec | 109 %-7 Sec | 150 %-0.1 Sec | [5 empty] | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 0
56 | Seoni | Bina-PG | 1 | WRTS-1 | WRTS-1 | WRTS-2 | 292 | Quad Bersimis | 2194.4416 | 686.2 | 240 | Yes | 240 | - | 108 % -5 Sec | 150 %-0.1 Sec | 108 % -5 Sec | 150 %-0.1 Sec | [5 empty] | 1 | 0 | 0 | 0 | 0 | 1 | 0 | 0
57 | Seoni | Wardha | 1 | WRTS-1 | WRTS-1 | WRTS-1 | 261 | Quad Bersimis | 2194.4416 | 613.35 | 240 | Yes | - | - | 109 %- 7 Sec | 150 %-0.1 Sec | 109 %- 7 Sec | 150 %-0.1 Sec | [5 empty] | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0
58 | Seoni | Wardha | 2 | WRTS-1 | WRTS-1 | WRTS-1 | 261 | Quad Bersimis | 2194.4416 | 613.35 | 240 | Yes | - | - | 108 %-7 Sec | 150 %-0.1 Sec | 108 %-7 Sec | 150 %-0.1 Sec | [5 empty] | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0
59 | Sipat | Bilaspur | 1 | WRTS-1 | NTPC | WRTS-1 | 22 | Quad Bersimis | 2194.4416 | 51.7 | 240 | Yes | - | - | 109%-5 Sec | 150 %-0.1 Sec | 109 %-5 Sec | 150 %-0.1 Sec | [5 empty] | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0
60 | Sipat | Bilaspur | 2 | WRTS-1 | NTPC | WRTS-1 | 22 | Quad Bersimis | 2194.4416 | 51.7 | 240 | Yes | - | - | 108 %-6 Sec | 150 %-0.1 Sec | 108 %-6 Sec | 150 %-0.1 Sec | [5 empty] | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0
61 | Solapur | Raichur | 1 | SRTS-1 | WRTS-1 | SRTS-1 | 208 | Quad Bersimis | 2194.4416 | 488.8 | 240 | Yes | 240 | Yes | 110 %-4 Sec | 140 %-0.1 Sec | 109 %-5Sec | 150 %-0.1 Sec | [5 empty] | 1 | 0 | 0 | 0 | 1 | 0 | 0 | 0
62 | Solapur | Raichur | 2 | SRTCL | WRTS-1 | SRTS-1 | 208 | Quad Bersimis | 2194.4416 | 488.8 | 240 | Yes | 240 | Yes | 110 %-4 Sec | 140 %-0.1 Sec | 108 %-7Sec | 150 %-0.1 Sec | [5 empty] | 1 | 0 | 0 | 0 | 1 | 0 | 0 | 0
63 | Tiroda | Koradi(III) | 1 | MEGPTCL | APML | MEGPTCL | 136 | Quad Bersimis | 2194.4416 | 319.6 | 240 | Yes | 240 | Yes | 109 %-5 Sec | 150 %-0.1 Sec | 109 %-5 Sec | 150 %-0.1 Sec | [5 empty] | 1 | 0 | 0 | 0 | 1 | 0 | 0 | 0
64 | Tiroda | Koradi(III) | 2 | MEGPTCL | APML | MEGPTCL | 138 | Quad Bersimis | 2194.4416 | 324.3 | 240 | Yes | 240 | Yes | 109 %-7 Sec | 150 %-0.1 Sec | 109 %-7 Sec | 150 %-0.1 Sec | [5 empty] | 1 | 0 | 0 | 0 | 1 | 0 | 0 | 0
65 | Vadodora-PS | Indore-PG | 1 | WRTS-2 | WRTS-2 | WRTS-2 | 293 | Quad Bersimis | 2194.4416 | 688.55 | 240 | - | 240 | Yes | 110 %-7 Sec | 140 %-0.15 Sec | 110 %-7 Sec | 140 %-0.15 Sec | [5 empty] | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 0
66 | Vadodora-PS | Dhule-BDTCL | 1 | WRTS-2 | WRTS-2 | BDTCL | 268 | Quad Bersimis | 2194.4416 | 629.8 | 240 | - | 240 | Yes | 110 %-5 Sec | 140 %-0.15 Sec | 110 %-5 Sec | 140 %-0.15 Sec | [5 empty] | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 0
67 | Wardha | Raipur-PS(Durg) | 1 | WRTS-1 | WRTS-1 | WRTS-1 | 370 | Hexa Zebra | 2470.0035 | 984.2 | 330 | - | 240 | Yes | 109 %-6 Sec | 150 %-0.1 Sec | 109 %-6 Sec | 150 %-0.1 Sec | [5 empty] | 0 | 0 | 0 | 1 | 1 | 0 | 0 | 0
68 | Wardha | Raipur-PS(Durg) | 2 | WRTS-1 | WRTS-1 | WRTS-1 | 370 | Hexa Zebra | 2470.0035 | 984.2 | 330 | - | 240 | Yes | 108 %-5 Sec | 150 %-0.1 Sec | 110 %-5Sec | 140 %-0.1 Sec | [5 empty] | 0 | 0 | 0 | 1 | 1 | 0 | 0 | 0
* 765 kV line charged at 400 kV, # Future Lines | [6 empty] | 16584 |  |  |  | 15060 | Total | 12120 |  | 107 %-5 Sec | 150 %-0.1 Sec | 107 %-5 Sec | 150 %-0.1 Sec | [5 empty] | 35 | 14 | 6 | 4 | 21 | 24 | 4 | 0
[15 empty] | 107 %-7 Sec | 150 %-0.1 Sec | 107 %-7 Sec | 150 %-0.1 Sec | [5 empty] | 8400 | 3360 | 1980 | 1320 | 5040 | 5760 | 1320 | 0
[26 empty] | 15060 |  |  |  | 12120
27180
7710
34890

## 765kV BRs
Sr. No. | Name of S/S | Owner | Nos of Reactor | Total MVAR | Rated Voltage | 240 |  | 330
1 | Akola(2) | MEGPTCL | 3X80 | 240 | 800 | 1 | 3
2 | Aurangabad-PG | PGCIL | 3X80 | 240 | 800 | 1 | 3
3 | Bhopal-BDTCL | BDTCL | 3X80 | 240 | 800 | 1 | 3
4 | Bilaspur | PGCIL | 3X80 | 240 | 800 | 1 | 3
5 | Bina-NHPTL | NHPTL | - | - | -
6 | Bina-PG | PGCIL | 3X80 + 3X80 | 480 | 800 | 2 | 6
7 | Champa | PGCIL | 3X80 | 240 | 800 | 1 | 3
8 | Dharamjaygarh | PGCIL | 3X110 + 3X110 | 660 | 800 |  | 0 | 2
9 | Dhule-BDTCL | BDTCL | 3X80 | 240 | 800 | 1 | 3
10 | Ektuni (Aurangabad(3)) | MSETCL | 3X80 | 240 | 800 | 1 | 3
11 | Gwalior | PGCIL | 3X80 | 240 | 800 | 1 | 3
12 | Indore-PG | PGCIL | 3X80 + 3X80 | 480 | 800 | 2 | 6
13 | Jabalpur-PS | PGCIL | 3X80 + 3X80 | 480 | 800 | 2 | 6
14 | Koradi(III) | MEGPTCL | 3X80 | 240 | 800 | 1 | 3
15 | Pune-PG(Shikrapur) | PGCIL | 3X80 | 240 | 800 | 1 | 3
16 | Raigarh-PS(Kotra) | PGCIL | 3X80 | 240 | 800 | 1 | 3
17 | Raipur-PS(Durg) | PGCIL | 3X80 | 240 | 800 | 1 | 3
18 | Sasan | SPL | 3X80 | 240 | 800 | 1 | 3
19 | Satna | PGCIL | 3X80 + 3X80 | 480 | 800 | 2 | 6
20 | Seoni | PGCIL | 3X80 | 240 | 800 | 1 | 3
21 | Sipat | NTPC | 3X80 | 240 | 800 | 1 | 3
22 | Solapur | PGCIL | 3X80 | 240 | 800 | 1 | 3
23 | Tamnar | PGCIL | 3X80 | 240 | 800 | 1 | 3
24 | Tiroda | MEGPTCL | 3X80 | 240 | 800 | 1 | 3
25 | Vadodora-PS | PGCIL | 3X80 | 240 | 800 | 1 | 3
26 | Vindhyachal-PS | PGCIL | 3X80 | 240 | 800 | 1 | 3
27 | Wardha | PGCIL | 3X80 + 3X110 | 570 | 800 | 1 | 3 | 1
|  | Total | 9X110+87X80 | 7950 |  | 29 | 87

## 765 kV SS Res
Sr. No. | Name of S/S | S/S Owner | Lines | ID | km | Conductor Type | LRs | LRs S/W | BRs | Total MVAR | Rated Voltage | 240 MVAR SLRs | 240 MVAR NSLRs | 330 MVAR SLRs | 330 MVAR NSLRs
1 | Akola(2) | MEGPTCL | Ektuni (Aurangabad(3)) | 2 | 219 | Quad Bersimis | 240 | Yes | 1x240 | MEGPTCL | MSETCL | 1 | 0 | 0 | 0
|  |  | Ektuni (Aurangabad(3))# | 1 | 219 | Quad Bersimis | 240 | Yes |  | MEGPTCL | WRTS-1 | 1 | 0 | 0 | 0
|  |  | Koradi(III) | 1 | 222 | Quad Bersimis | 240 | - |  | MEGPTCL | MEGPTCL | 0 | 1 | 0 | 0
|  |  | Koradi(III) | 2 | 222 | Quad Bersimis | 240 | - |  | MEGPTCL | MEGPTCL | 0 | 1 | 0 | 0
|  | Total MVAR |  |  |  |  | 960 |  | 240 |  |  | 2 | 2 | 0 | 0 | 960
2 | Aurangabad-PG | PGCIL | Wardha | 1 | 348 | Hexa Zebra | 240 | - | 1x240 | WRTS-1 | WRTS-1 | 0 | 1 | 0 | 0
|  |  | Wardha | 2 | 348 | Hexa Zebra | 240 | - |  | WRTS-1 | WRTS-1 | 0 | 1 | 0 | 0
|  |  | Wardha | 3 | 370 | Hexa Zebra | 240 | - |  | WRTS-1 | WRTS-1 | 0 | 1 | 0 | 0
|  |  | Wardha | 4 | 370 | Hexa Zebra | 240 | - |  | WRTS-1 | WRTS-1 | 0 | 1 | 0 | 0
|  |  | Solapur | 1 | 279 | Hexa Zebra | 240 | Yes |  | WRTS-1 | WRTS-1 | 1 | 0 | 0 | 0
|  |  | Solapur | 2 | 279 | Hexa Zebra | 240 | Yes |  | WRTS-1 | WRTS-1 | 1 | 0 | 0 | 0
|  |  | Dhule-BDTCL | 1 | 192 | Quad Bersimis | - | - |  | BDTCL | BDTCL | 0 | 0 | 0 | 0
|  | Total MVAR |  |  |  |  | 1440 |  | 240 |  |  | 2 | 4 | 0 | 0 | 1440
3 | Bhopal-BDTCL | BDTCL | Indore-PG | 1 | 176 | Quad Bersimis | 240 | Yes | 1x240 | BDTCL | WRTS-2 | 1 | 0 | 0 | 0
|  |  | Jabalpur-PS | 1 | 260 | Quad Bersimis | 240 | - |  | BDTCL | WRTS-2 | 0 | 1 | 0 | 0
|  | Total MVAR |  |  |  |  | 480 |  | 240 |  |  | 1 | 1 | 0 | 0 | 480
4 | Bilaspur | PGCIL | Seoni | 1 | 333 | Quad Bersimis | 240 | Yes | 1x240 | WRTS-1 | WRTS-1 | 1 | 0 | 0 | 0
|  |  | Seoni | 2 | 335 | Quad Bersimis | 240 | Yes |  | WRTS-1 | WRTS-1 | 1 | 0 | 0 | 0
|  |  | Dharamjaygarh | 1 | 89 | Quad Bersimis | 240 | Yes |  | WRTS-1 | WRTS-1 | 1 | 0 | 0 | 0
|  |  | Sipat | 1 | 22 | Quad Bersimis | - | - |  | WRTS-1 | NTPC | 0 | 0 | 0 | 0
|  |  | Sipat | 2 | 22 | Quad Bersimis | - | - |  | WRTS-1 | NTPC | 0 | 0 | 0 | 0
|  | Total MVAR |  |  |  |  | 720 |  | 240 |  |  | 3 | 0 | 0 | 0 | 720
5 | Bina-NHPTL | NHPTL | Bina-PG | 1 | 0.2 | Quad Bersimis | - | - |  |  |  | 0 | 0 | 0 | 0
|  | Total MVAR |  |  |  |  | - | - | - |  |  | 0 | 0 | 0 | 0
6 | Bina-PG | PGCIL | Gwalior | 1 | 235 | Quad Bersimis | 240 | - | 2x240 | WRTS-2 | WRTS-2 | 0 | 1 | 0 | 0
|  |  | Jabalpur-PS | 3 | 236 | Quad Bersimis | 240 | - |  | WRTS-2 | WRTS-2 | 0 | 1 | 0 | 0
|  |  | Gwalior | 2 | 235 | Quad Bersimis | 240 | - |  | WRTS-2 | WRTS-2 | 0 | 1 | 0 | 0
|  |  | Gwalior | 3 | 231 | Quad Bersimis | 240 | Yes |  | WRTS-2 | WRTS-2 | 1 | 0 | 0 | 0
|  |  | Indore-PG | 1 | 310 | Quad Bersimis | 240 | Yes |  | WRTS-2 | WRTS-2 | 1 | 0 | 0 | 0
|  |  | Jabalpur-PS | 1 | 230 | Quad Bersimis | 240 | - |  | WRTS-2 | WRTS-2 | 0 | 1 | 0 | 0
|  |  | Jabalpur-PS | 2 | 230 | Quad Bersimis | 240 | - |  | JTCL | WRTS-2 | 0 | 1 | 0 | 0
|  |  | Bina-NHPTL | 1 | 0.2 | Quad Bersimis | - | - |  | WRTS-2 | WRTS-2 | 0 | 0 | 0 | 0
|  |  | Satna | 1 | 274 | Quad Bersimis | 240 | - |  | WRTS-2 | WRTS-2 | 0 | 1 | 0 | 0
|  |  | Satna | 2 | 276 | Quad Bersimis | 240 | - |  |  |  | 0 | 1 | 0 | 0
|  |  | Seoni | 1 | 292 | Quad Bersimis | 240 | - |  | WRTS-1 | WRTS-1 | 0 | 1 | 0 | 0
|  | Total MVAR |  |  |  |  | 2400 |  | 480 |  |  | 2 | 8 | 0 | 0 | 2400
7 | Champa | PGCIL | Raigarh-PS(Kotra) | 1 | 96 | Quad Bersimis | - | - | 1x240 |  |  | 0 | 0 | 0 | 0
|  |  | Raipur-PS(Durg) | 1 | 153 | Quad Bersimis | - | - |  |  |  | 0 | 0 | 0 | 0
|  | Total MVAR |  |  |  |  | 0 |  | 240 |  |  | 0 | 0 | 0 | 0 | 0
8 | Dharamjaygarh | PGCIL | Ranchi | 1 | 301 | Quad Bersimis | 330 | - | 2x330 |  |  | 0 | 0 | 0 | 1
|  |  | Ranchi | 2 | 303 | Quad Bersimis | 330 | - |  |  |  | 0 | 0 | 0 | 1
|  |  | Raipur-PS(Durg) | 2 | 200 | Quad Bersimis | 240 | - |  |  |  | 0 | 1 | 0 | 0
|  |  | Jharsuguda | 1 | 303 | Hexa Zebra | 330 | Yes |  |  |  | 0 | 0 | 1 | 0
|  |  | Jharsuguda | 2 | 303 | Hexa Zebra | 330 | Yes |  |  |  | 0 | 0 | 1 | 0
|  |  | Jabalpur-PS | 1 | 424 | Hexa Zebra | 330 | Yes |  |  |  | 0 | 0 | 1 | 0
|  |  | Jabalpur-PS | 2 | 424 | Hexa Zebra | 330 | Yes |  |  |  | 0 | 0 | 1 | 0
|  |  | Jabalpur-PS | 3 | 379 | Hexa Zebra | 330 | Yes |  |  |  | 0 | 0 | 1 | 0
|  |  | Jabalpur-PS | 4 | 379 | Hexa Zebra | 330 | Yes |  |  |  | 0 | 0 | 1 | 0
|  |  | Bilaspur | 1 | 89 | Quad Bersimis | - | - |  |  |  | 0 | 0 | 0 | 0
|  | Total MVAR |  |  |  |  | 2880 |  | 660 |  |  | 0 | 1 | 6 | 2 | 2880
9 | Dhule-BDTCL | BDTCL | Aurangabad-PG | 1 | 192 | Quad Bersimis | 240 | Yes | 240 |  |  | 1 | 0 | 0 | 0
|  |  | Vadodora-PS | 1 | 268 | Quad Bersimis | 240 | Yes |  |  |  | 1 | 0 | 0 | 0
|  | Total MVAR |  |  |  |  | 480 |  | 240 |  |  | 2 | 0 | 0 | 0 | 480
10 | Ektuni (Aurangabad(3)) | MSETCL | Akola(2) | 2 | 219 | Quad Bersimis | 240 | - | 240 |  |  | 0 | 1 | 0 | 0
|  |  | Akola(2) | 1 | 219 | Quad Bersimis | 240 | - |  |  |  | 0 | 1 | 0 | 0
|  | Total MVAR |  |  |  |  | 480 |  | 240 |  |  | 0 | 2 | 0 | 0 | 480
11 | Gwalior | PGCIL | Bina-PG | 1 | 235 | Quad Bersimis | 240 | Yes | 240 |  |  | 1 | 0 | 0 | 0
|  |  | Bina-PG | 2 | 235 | Quad Bersimis | 240 | Yes |  |  |  | 1 | 0 | 0 | 0
|  |  | Bina-PG | 3 | 231 | Quad Bersimis | 240 | Yes |  |  |  | 1 | 0 | 0 | 0
|  |  | Agra | 1 | 129 | Quad Bersimis | - | - |  |  |  | 0 | 0 | 0 | 0
|  |  | Agra | 2 | 128 | Quad Bersimis | - | - |  |  |  | 0 | 0 | 0 | 0
|  |  | Jaipur | 1 | 304 | Quad Bersimis | 240 | Yes |  |  |  | 1 | 0 | 0 | 0
|  |  | Jaipur | 2 | 311 | Quad Bersimis | 240 | Yes |  |  |  | 1 | 0 | 0 | 0
|  |  | Satna | 1 | 337 | Quad Bersimis | 240 | - |  |  |  | 0 | 1 | 0 | 0
|  |  | Satna | 2 | 337 | Quad Bersimis | 240 | - |  |  |  | 0 | 1 | 0 | 0
|  | Total MVAR |  |  |  |  | 1680 |  | 240 |  |  | 5 | 2 | 0 | 0 | 1680
12 | Indore-PG | PGCIL | Bhopal-BDTCL | 1 | 176 | Quad Bersimis | 240 | - | 2x240 |  |  | 0 | 1 | 0 | 0
|  |  | Bina-PG | 1 | 310 | Quad Bersimis | 240 | - |  |  |  | 0 | 1 | 0 | 0
|  |  | Vadodora-PS | 1 | 293 | Quad Bersimis | 240 | Yes |  |  |  | 1 | 0 | 0 | 0
|  | Total MVAR |  |  |  |  | 720 |  | 480 |  |  | 1 | 2 | 0 | 0 | 720
13 | Jabalpur-PS | PGCIL | Bina-PG | 1 | 230 | Quad Bersimis | 240 | Yes | 2x240 | 480 | 800 | 1 | 0 | 0 | 0
|  |  | Bina-PG | 2 | 230 | Quad Bersimis | 240 | Yes |  |  |  | 1 | 0 | 0 | 0
|  |  | Bina-PG | 3 | 236 | Quad Bersimis | 240 | Yes |  |  |  | 1 | 0 | 0 | 0
|  |  | Dharamjaygarh | 1 | 424 | Hexa Zebra | 240 | - |  |  |  | 0 | 1 | 0 | 0
|  |  | Dharamjaygarh | 2 | 424 | Hexa Zebra | 240 | - |  |  |  | 0 | 1 | 0 | 0
|  |  | Dharamjaygarh | 3 | 379 | Hexa Zebra | 240 | - |  |  |  | 0 | 1 | 0 | 0
|  |  | Dharamjaygarh | 4 | 379 | Hexa Zebra | 240 | - |  |  |  | 0 | 1 | 0 | 0
|  |  | Bhopal-BDTCL | 1 | 260 | Quad Bersimis | 240 | Yes |  |  |  | 1 | 0 | 0 | 0
|  | Total MVAR |  |  |  |  | 1920 |  | 480 |  |  | 4 | 4 | 0 | 0 | 1920
14 | Kholpaur-PG* | PGCIL | Kudgi* | 1 | 191 | Hexa Zebra | - | - | - |  |  | 0 | 0 | 0 | 0
|  |  | Kudgi* | 2 | 191 | Hexa Zebra | - | - |  |  |  | 0 | 0 | 0 | 0
|  | Total MVAR |  |  |  |  | - |  | - |  |  | 0 | 0 | 0 | 0 | 0
15 | Koradi(III) | MEGPTCL | Akola(2) | 1 | 222 | Quad Bersimis | 240 | Yes | 1x240 |  |  | 1 | 0 | 0 | 0
|  |  | Akola(2) | 2 | 222 | Quad Bersimis | 240 | Yes |  |  |  | 1 | 0 | 0 | 0
|  |  | Tiroda | 1 | 136 | Quad Bersimis | 240 | Yes |  |  |  | 1 | 0 | 0 | 0
|  |  | Tiroda | 2 | 138 | Quad Bersimis | 240 | Yes |  |  |  | 1 | 0 | 0 | 0
|  | Total MVAR |  |  |  |  | 960 |  | 240 |  |  | 4 | 0 | 0 | 0 | 960
16 | Pune-PG(Shikrapur) | PGCIL | Solapur | 1 | 270 | Quad Bersimis | 240 | Yes | 1x240 |  |  | 1 | 0 | 0 | 0
|  | Total MVAR |  |  |  |  | 240 |  | 240 |  |  | 1 | 0 | 0 | 0 | 240
17 | Raigarh-PS(Kotra) | PGCIL | Raipur-PS(Durg) | 1 | 235 | Hexa Zebra | 240 | Yes | 1x240 |  |  | 1 | 0 | 0 | 0
|  |  | Raipur-PS(Durg) | 2 | 235 | Hexa Zebra | 240 | Yes |  |  |  | 1 | 0 | 0 | 0
|  |  | Tamnar | 1 | 48 | Hexa Zebra | - | - |  |  |  | 0 | 0 | 0 | 0
|  |  | Tamnar | 2 | 48 | Hexa Zebra | - | - |  |  |  | 0 | 0 | 0 | 0
|  |  | Champa | 1 | 96 | Quad Bersimis | - | - |  |  |  | 0 | 0 | 0 | 0
|  | Total MVAR |  |  |  |  | 480 |  | 240 |  |  | 2 | 0 | 0 | 0 | 480
18 | Raipur-PS(Durg) | PGCIL | Champa | 1 | 153 | Quad Bersimis | 240 | Yes | 1x240 | WRTS-1 | WRTS-1 | 1 | 0 | 0 | 0
|  |  | Dharamjaygarh | 2 | 200 | Quad Bersimis | - | - |  | WRTS-1 | WRTS-1 | 0 | 0 | 0 | 0
|  |  | Raigarh-PS(Kotra) | 1 | 235 | Hexa Zebra | 240 | - |  | WRTS-1 | WRTS-1 | 0 | 1 | 0 | 0
|  |  | Raigarh-PS(Kotra) | 2 | 235 | Hexa Zebra | 240 | - |  | WRTS-1 | WRTS-1 | 0 | 1 | 0 | 0
|  |  | Wardha | 1 | 370 | Hexa Zebra | 240 | Yes |  | WRTS-1 | WRTS-1 | 1 | 0 | 0 | 0
|  |  | Wardha | 2 | 370 | Hexa Zebra | 240 | Yes |  | WRTS-1 | WRTS-1 | 1 | 0 | 0 | 0
|  | Total MVAR |  |  |  |  | 1200 |  | 240 |  |  | 3 | 2 | 0 | 0 | 1200
19 | Sasan | SPL | Satna | 1 | 246 | Quad Bersimis | 240 | Yes | 1x240 | 240 | 800 | 1 | 0 | 0 | 0
|  |  | Satna | 2 | 243 | Quad Bersimis | 240 | Yes |  |  |  | 1 | 0 | 0 | 0
|  |  | Vindhyachal-PS | 1 | 6 | Quad Bersimis | - | - |  |  |  | 0 | 0 | 0 | 0
|  | Total MVAR |  |  |  |  | 480 |  | 240 |  |  | 2 | 0 | 0 | 0 | 480
20 | Satna | PGCIL | Gwalior | 1 | 337 | Quad Bersimis | 240 | Yes | 2x240 | WRTS-2 | WRTS-2 | 1 | 0 | 0 | 0
|  |  | Gwalior | 2 | 337 | Quad Bersimis | 240 | Yes |  | WRTS-2 | WRTS-2 | 1 | 0 | 0 | 0
|  |  | Bina-PG | 1 | 274 | Quad Bersimis | 240 | Yes |  | WRTS-2 | WRTS-2 | 1 | 0 | 0 | 0
|  |  | Bina-PG | 2 | 276 | Quad Bersimis | 240 | Yes |  | WRTS-2 | WRTS-2 | 1 | 0 | 0 | 0
|  |  | Vindhyachal-PS | 1 | 237 | Quad Bersimis | 240 | - |  | WRTS-2 | WRTS-2 | 0 | 1 | 0 | 0
|  |  | Vindhyachal-PS | 2 | 237 | Quad Bersimis | 240 | - |  | WRTS-2 | WRTS-2 | 0 | 1 | 0 | 0
|  |  | Sasan | 1 | 246 | Quad Bersimis | 240 | - |  | WRTS-2 | SPL | 0 | 1 | 0 | 0
|  |  | Sasan | 2 | 243 | Quad Bersimis | 240 | - |  | WRTS-2 | SPL | 0 | 1 | 0 | 0
|  | Total MVAR |  |  |  |  | 1920 |  | 480 |  |  | 4 | 4 | 0 | 0 | 1920
21 | Seoni | PGCIL | Bilaspur | 1 | 333 | Quad Bersimis | 240 | - | 1x240 | 240 | 800 | 0 | 1 | 0 | 0
|  |  | Bilaspur | 2 | 335 | Quad Bersimis | 240 | - |  |  |  | 0 | 1 | 0 | 0
|  |  | Bina-PG | 1 | 292 | Quad Bersimis | 240 | Yes |  |  |  | 1 | 0 | 0 | 0
|  |  | Wardha | 1 | 261 | Quad Bersimis | 240 | Yes |  |  |  | 1 | 0 | 0 | 0
|  |  | Wardha | 2 | 261 | Quad Bersimis | 240 | Yes |  |  |  | 1 | 0 | 0 | 0
|  | Total MVAR |  |  |  |  | 1200 |  | 240 |  |  | 3 | 2 | 0 | 0 | 1200
22 | Sipat | NTPC | Bilaspur | 1 | 22 | Quad Bersimis | 240 | Yes | 1x240 | 240 | 800 | 1 | 0 | 0 | 0
|  |  | Bilaspur | 2 | 22 | Quad Bersimis | 240 | Yes |  |  |  | 1 | 0 | 0 | 0
|  | Total MVAR |  |  |  |  | 480 |  | 240 |  |  | 2 | 0 | 0 | 0 | 480
23 | Solapur | PGCIL | Aurangabad-PG | 1 | 279 | Hexa Zebra | 240 | Yes | 1x240 | 240 | 800 | 1 | 0 | 0 | 0
|  |  | Aurangabad-PG | 2 | 279 | Hexa Zebra | 240 | Yes |  |  |  | 1 | 0 | 0 | 0
|  |  | Pune-PG(Shikrapur) | 1 | 270 | Quad Bersimis | 240 | Yes |  |  |  | 1 | 0 | 0 | 0
|  |  | Raichur | 1 | 208 | Quad Bersimis | 240 | Yes |  |  |  | 1 | 0 | 0 | 0
|  |  | Raichur | 2 | 208 | Quad Bersimis | 240 | Yes |  |  |  | 1 | 0 | 0 | 0
|  | Total MVAR |  |  |  |  | 1200 |  | 240 |  |  | 5 | 0 | 0 | 0 | 1200
24 | Tamnar | PGCIL | Raigarh-PS(Kotra) | 1 | 48 | Hexa Zebra | - | - | 1x240 | 240 | 800 | 0 | 0 | 0 | 0
|  |  | Raigarh-PS(Kotra) | 2 | 48 | Hexa Zebra | - | - |  |  |  | 0 | 0 | 0 | 0
|  | Total MVAR |  |  |  |  | - |  | 240 |  |  | 0 | 0 | 0 | 0 | 0
25 | Tiroda | MEGPTCL | Koradi(III) | 1 | 136 | Quad Bersimis | 240 | Yes | 1x240 | 240 | 800 | 1 | 0 | 0 | 0
|  |  | Koradi(III) | 2 | 138 | Quad Bersimis | 240 | Yes |  |  |  | 1 | 0 | 0 | 0
|  | Total MVAR |  |  |  |  | 480 |  | 240 |  |  | 2 | 0 | 0 | 0 | 480
26 | Vadodora-PS | PGCIL | Indore-PG | 1 | 293 | Quad Bersimis | 240 | - | 1x240 | 240 | 800 | 0 | 1 | 0 | 0
|  |  | Dhule-BDTCL | 1 | 268 | Quad Bersimis | 240 | - |  |  |  | 0 | 1 | 0 | 0
|  | Total MVAR |  |  |  |  | 480 |  | 240 |  |  | 0 | 2 | 0 | 0 | 480
27 | Vindhyachal-PS | PGCIL | Sasan | 1 | 6 | Quad Bersimis | - | - | 1x240 | 240 | 800 | 0 | 0 | 0 | 0
|  |  | Satna | 1 | 237 | Quad Bersimis | 240 | Yes |  |  |  | 1 | 0 | 0 | 0
|  |  | Satna | 2 | 237 | Quad Bersimis | 240 | Yes |  |  |  | 1 | 0 | 0 | 0
|  | Total MVAR |  |  |  |  | 480 |  | 240 |  |  | 2 | 0 | 0 | 0 | 480
28 | Wardha | PGCIL | Aurangabad-PG | 1 | 348 | Hexa Zebra | 330 | Yes | 1x240+1x330 | 570 | 800 | 0 | 0 | 1 | 0
|  |  | Aurangabad-PG | 2 | 348 | Hexa Zebra | 330 | Yes |  |  |  | 0 | 0 | 1 | 0
|  |  | Aurangabad-PG | 3 | 370 | Hexa Zebra | 330 | Yes |  |  |  | 0 | 0 | 1 | 0
|  |  | Aurangabad-PG | 4 | 370 | Hexa Zebra | 330 | Yes |  |  |  | 0 | 0 | 1 | 0
|  |  | Seoni | 1 | 261 | Quad Bersimis | - | - |  |  |  | 0 | 0 | 0 | 0
|  |  | Seoni | 2 | 261 | Quad Bersimis | - | - |  |  |  | 0 | 0 | 0 | 0
|  |  | Raipur-PS(Durg) | 1 | 370 | Hexa Zebra | 330 | - |  |  |  | 0 | 0 | 0 | 1
|  |  | Raipur-PS(Durg) | 2 | 370 | Hexa Zebra | 330 | - |  |  |  | 0 | 0 | 0 | 1
|  | Total MVAR |  |  |  |  | 1980 |  | 570 |  |  | 0 | 0 | 4 | 2 | 1980
* Charged at 400 kV

## 400 kV BRs
S.No | Substation | Owner | Nos of Reactor | Total MVAR | Rated Voltage |  | 50 MVAR | 63 MVAR | 80 MVAR | 125 MVAR
1 | Amreli | GETCO | 1X50 + 1X125 | 175 | 420 |  | 1 |  |  | 1 | 175
2 | APL-Mundra | APL | 2X80 + 1X125 | 285 | 420 |  |  |  | 2 | 1 | 285
3 | Astha | MPPTCL | 1x50 | 50 | 420 |  | 1 |  |  |  | 50
4 | Asoj | GETCO | 1X50 | 50 | 420 |  | 1 |  |  |  | 50
5 | Aurangabad-PG | PGCIL | 1X125 | 125 | 420 |  |  |  |  | 1 | 125
6 | Bableshwar | MSETCL | 2X80 | 160 | 420 |  |  |  | 2 |  | 160
7 | Bachau | PGCIL | 1X63 + 1X125 | 188 | 420 |  |  | 1 |  | 1 | 188
8 | Bhadrawati | PGCIL | 1X50 | 50 | 420 |  | 1 |  |  |  | 50
9 | Bhatapara | PGCIL | 1X125 | 125 | 420 |  |  |  |  | 1 | 125
10 | Bhopal-BDTCL | BDTCL | 1X125 | 125 | 420 |  |  |  |  | 1 | 125
11 | Bhopal-MP | MPPTCL | 1X125 + 1x80 | 205 | 420 | 80 added |  |  | 1 | 1 | 205
12 | Bhusawal (Khadka) | MSETCL | 1X50 | 50 | 420 |  | 1 |  |  |  | 50
13 | Bina-MP | MPPTCL | 1X50 | 50 | 420 |  | 1 |  |  |  | 50
14 | Bina-PG | PGCIL | 1X125 | 125 | 420 |  |  |  |  | 1 | 125
15 | Birsingpur | MPPTCL | 1X50 | 50 | 420 |  | 1 |  |  |  | 50
16 | CGPL | CGPL | 1x63 | 63 | 420 |  |  | 1 |  |  | 63
17 | Champa | PGCIL | 1x80 | 80 | 420 |  |  |  | 1 |  | 80
18 | Chhegaon | MPPTCL | 1x50 | 50 | 420 |  | 1 |  |  |  | 50
19 | Chorania | GETCO | 1X50 + 1X125 | 175 | 420 |  | 1 |  |  | 1 | 175
20 | Damoh | PGCIL | 1X63 + 1X125 | 188 | 420 |  |  | 1 |  | 1 | 188
21 | Dehgam | PGCIL | 1X63 + 1X125 | 188 | 420 |  |  | 1 |  | 1 | 188
22 | DGEN | DGEN | 1X125 | 125 | 420 |  |  |  |  | 1 | 125
23 | Dhariwal | DIL | 1x80 | 80 | 420 |  |  |  | 1 |  | 80
24 | Dhariwal-MS | DIL | 1x80 | 80 | 420 |  |  |  | 1 |  | 80
25 | Dhule-MS | MSETCL | 1X80 | 80 | 420 |  |  |  | 1 |  | 80
26 | EMCO | GMR | 1X80 | 80 | 420 |  |  |  | 1 |  | 80
27 | Essar_Mahan | ESSAR | 1X80 | 80 | 420 |  |  |  | 1 |  | 80
28 | Gandhar | NTPC | 1X50 | 50 | 420 |  | 1 |  |  |  | 50
29 | GMR-CG | GMR | 1x125 | 125 | 420 |  |  |  |  | 1 | 125
30 | Gwalior | PGCIL | 3X125 | 375 | 420 |  |  |  |  | 3 | 375
31 | Hadala | GETCO | 1X50 + 1X125 | 175 | 420 |  | 1 |  |  | 1 | 175
32 | Indore-PG | PGCIL | 1X125 + 1X63 | 188 | 420 |  |  | 1 |  | 1 | 188
33 | Itarsi | PGCIL | 2X125 + 1X50 | 300 | 420 |  | 1 |  |  | 2 | 300
34 | Jabalpur | PGCIL | 1X125 + 1X63 | 188 | 420 |  |  | 1 |  | 1 | 188
35 | Jabalpur (PS) | PGCIL | 2X125 | 250 | 420 |  |  |  |  | 2 | 250
36 | Jaigad | JPTL | 2x50 | 100 | 420 |  | 2 |  |  |  | 100
37 | Jetpur | GETCO | 1X50 + 1X63 | 113 | 420 |  | 1 | 1 |  |  | 113
38 | JPL | JPL | 1x125 | 125 | 420 |  |  |  |  | 1 | 125
39 | JP-Nigrie | JPVL | 1X125 | 125 | 420 |  |  |  |  | 1 | 125
40 | Julwania | MPPTCL | 1x50 | 50 | 420 |  | 1 |  |  |  | 50
41 | Kala | PGCIL | 1X80 | 80 | 420 |  |  |  | 1 |  | 80
42 | Karad | MSETCL | 1X80 | 80 | 420 |  |  |  | 1 |  | 80
43 | Kasor | GETCO | 1X50 + 1X125 | 175 | 420 |  | 1 |  |  | 1 | 175
44 | Khandwa | PGCIL | 2X125 | 250 | 420 |  |  |  |  | 2 | 250
45 | Kharghar | MSETCL | 1X80 | 80 | 420 |  |  |  | 1 |  | 80
46 | Kolhapur | MSETCL | 1X80 | 80 | 420 |  |  |  | 1 |  | 80
47 | Kolhapur-PG | PGCIL | 1x125 | 125 | 420 |  |  |  |  | 1 | 125
48 | Koradi | MSETCL | 1X50 | 50 | 420 |  | 1 |  |  |  | 50
49 | Kosamba | GETCO | 1X80 | 80 | 420 |  |  |  | 1 |  | 80
50 | Lonikhand | MSETCL | 1X50 | 50 | 420 |  | 1 |  |  |  | 50
51 | Magarawada | PGCIL | 1x80 | 80 | 420 |  |  |  | 1 |  | 80
52 | Mansar | GETCO | 1x63 | 63 | 420 | 80 |  | 1 |  |  | 63
53 | Mapusa | PGCIL | 1X50 | 50 | 420 |  | 1 |  |  |  | 50
54 | MB Power | MB Power | 1x125 | 125 | 420 |  |  |  |  | 1 | 125
55 | Mouda | NTPC | 1x80 | 80 | 420 |  |  |  | 1 |  | 80
56 | Nagda | MPPTCL | 2X50 | 100 | 420 |  | 2 |  |  |  | 100
57 | Nagothane | MSETCL | 1X80 | 80 | 420 |  |  |  | 1 |  | 80
58 | Nandgaonpeth | Rattan India | 1x80 | 80 | 420 |  |  |  | 1 |  | 80
59 | Navsari | PGCIL | 1X63 | 63 | 420 |  |  | 1 |  |  | 63
60 | Padghe | MSETCL | 1X80 | 80 | 420 |  |  |  | 1 |  | 80
61 | Parli-M | MSETCL | 1X50 | 50 | 420 |  | 1 |  |  |  | 50
62 | Parli-PG | PGCIL | 1X63 + 1X125 | 188 | 420 |  |  | 1 |  | 1 | 188
63 | Pirana-PG | PGCIL | 1X125 | 125 | 420 |  |  |  |  | 1 | 125
64 | Pithampur | MPPTCL | 1x50 | 50 | 420 |  | 1 |  |  |  | 50
65 | Pune-PG | PGCIL | 1X50 | 50 | 420 |  | 1 |  |  |  | 50
66 | Raigarh | PGCIL | 1X63 + 1X125 | 188 | 420 |  |  | 1 |  | 1 | 188
67 | Raigarh-PS(Kotra) | PGCIL | 1X80 | 80 | 420 |  |  |  | 1 |  | 80
68 | Raipur | PGCIL | 1X125 + 1X80 | 205 | 420 |  |  |  | 1 | 1 | 205
69 | Rajgarh | PGCIL | 1X125 | 125 | 420 |  |  |  |  | 1 | 125
70 | Ranchodpura | GETCO | 1X50 + 1X125 | 175 | 420 |  | 1 |  |  | 1 | 175
71 | RKM | RKM | 2x50 | 100 | 420 |  | 2 |  |  |  | 100
72 | Sami | APL | 1X50 | 50 | 420 |  | 1 |  |  |  | 50
73 | Satna | PGCIL | 1X50 + 1X63 | 113 | 420 |  | 1 | 1 |  |  | 113
74 | Satpura | MPPTCL | 2X63 | 126 | 420 |  |  | 2 |  |  | 126
75 | Seoni | PGCIL | 2x125 | 250 | 420 |  |  |  |  | 2 | 250
76 | Shujalpur | PGCIL | 1X63 + 1X125 | 188 | 420 |  |  | 1 |  | 1 | 188
77 | SKS | SKS | 1x50 | 50 | 420 |  | 1 |  |  |  | 50
78 | Soja | GETCO | 1X50 + 1X80 | 130 | 420 |  | 1 |  | 1 |  | 130
79 | Solapur-PG | PGCIL | 1X63 | 63 | 420 |  |  | 1 |  |  | 63
80 | Tiroda | MEGPTCL | 2X80 | 160 | 420 |  |  |  | 2 |  | 160
81 | Uno-Sugen | TPL | 1X80 | 80 | 420 |  |  |  | 1 |  | 80
82 | Varsana | GETCO | 1X50 + 1X125 | 175 | 420 |  | 1 |  |  | 1 | 175
83 | Vindhyachal | NTPC | 1X63 + 1X50 | 113 | 420 |  | 1 | 1 |  |  | 113
84 | Vindhyachal-IV | NTPC | 1X80 | 80 | 420 |  |  |  | 1 |  | 80
85 | Vindhyachal-PS | PGCIL | 1X63 | 63 | 420 |  |  |  |  | 1 | 125
86 | Vindhyachal-V | NTPC | 1x125 | 125 | 420 |  |  | 1 |  |  | 63
87 | Wardha | PGCIL | 1X50 | 50 | 420 |  | 1 |  |  |  | 50
88 | Warora | ATIL | 1x125 | 125 | 420 |  |  |  |  | 1 | 125
89 | Zerda(Kansari) | GETCO | 1X50 + 1X125 | 175 | 420 | only 50 | 1 |  |  | 1 | 175
|  | Total | 50x36+18x63+28x80+43x125 | 10549 |  |  | 36 | 18 | 28 | 43 | 10549
[7 empty] | 1800 | 1134 | 2240 | 5375 | 10549

## 400kV SS and BRs
S.no | Substation | State | S/S Owner | Owner | Nos of Reactor | Total MVAR | Rated Voltage | 50x35+40x125+17x63+27x80
1 | ACBIL | [6 empty] | 9981
2 | Akola
3 | Akola(2)
4 | Amreli |  |  | GETCO | 1X50 + 1X125 | 175 | 420
5 | APL-Mundra |  |  | APL | 2X80 + 1X125 | 285 | 420
6 | Asoj |  |  | GETCO | 1X50 | 50 | 420
7 | Astha |  |  | MPPTCL | 1x50 | 50 | 420
8 | Athena |  |  | ACPL
9 | Aurangabad-M(Waluj)
10 | Aurangabad-PG |  |  | PGCIL | 1X125 | 125 | 420
11 | Bableshwar |  |  | MSETCL | 2X80 | 160 | 420
12 | Bachau |  |  | PGCIL | 1X63 + 1X125 | 188 | 420
13 | Balco
14 | Bhadrawati |  |  | PGCIL | 1X50 | 50 | 420
15 | Bhatapara |  |  | PGCIL | 1X125 | 125 | 420
16 | Bhilai
17 | Bhopal-BDTCL |  |  | BDTCL | 1X125 | 125 | 420
18 | Bhopal-MP |  |  | MPPTCL | 1X125 + 1x80 | 205 | 420
19 | Bhusawal (Khadka) |  |  | MSETCL | 1X50 | 50 | 420
20 | Bilaspur
21 | Bina-MP |  |  | MPPTCL | 1X50 | 50 | 420
22 | Bina-NHPTL |  |  | NHPTL
23 | Bina-NTS |  |  | PGCIL
24 | Bina-PG |  |  | PGCIL | 1X125 | 125 | 420
25 | Birsingpur |  |  | MPPTCL | 1X50 | 50 | 420
26 | Boisar
27 | CGPL |  |  | CGPL | 1x63 | 63 | 420
28 | Chakan
29 | Champa |  |  | PGCIL | 1x80 | 80 | 420
30 | Chandrapur
31 | Chandrapur-II
32 | Chhegaon |  |  | MPPTCL | 1x50 | 50 | 420
33 | Chorania |  |  | GETCO | 1X50 + 1X125 | 175 | 420
34 | Damoh |  |  | PGCIL | 1X63 + 1X125 | 188 | 420
35 | DB-Power
36 | Deepnagar
37 | Dehgam |  |  | PGCIL | 1X63 + 1X125 | 188 | 420
38 | DGEN |  |  | DGEN | 1X125 | 125 | 420
39 | Dhariwal |  |  | DIL | 1x80 | 80 | 420
40 | Dhariwal-MS |  |  | DIL | 1x80 | 80 | 420
41 | Dhule-BDTCL
42 | Dhule-MS |  |  | MSETCL | 1X80 | 80 | 420
43 | EMCO |  |  | GMR | 1X80 | 80 | 420
44 | Essar_Mahan |  |  | ESSAR | 1X80 | 80 | 420
45 | Gandhar |  |  | NTPC | 1X50 | 50 | 420
46 | GMR-CG |  |  | GMR | 1x125 | 125 | 420
47 | GPEC
48 | Gwalior |  |  | PGCIL | 3X125 | 375 | 420
49 | Hadala |  |  | GETCO | 1X50 + 1X125 | 175 | 420
50 | Hazira
51 | IEPL
52 | Indira Sagar
53 | Indore-MP
54 | Indore-PG |  |  | PGCIL | 1X125 + 1X63 | 188 | 420
55 | Itarsi |  |  | PGCIL | 2X125 + 1X50 | 300 | 420
56 | Jabalpur |  |  | PGCIL | 1X125 + 1X63 | 188 | 420
57 | Jabalpur (PS) |  |  | PGCIL | 2X125 | 250 | 420
58 | Jaigad |  |  | JPTL | 2x50 | 100 | 420
59 | Jejuri
60 | Jetpur |  |  | GETCO | 1X50 + 1X63 | 113 | 420
61 | Jhabua Power
62 | JP-Bina
63 | JPL |  |  | JPL | 1x125 | 125 | 420
64 | JPL_extn(Tamnar)
65 | JP-Nigrie |  |  | JPVL | 1X125 | 125 | 420
66 | Julwania |  |  | MPPTCL | 1x50 | 50 | 420
67 | Kala |  |  | PGCIL | 1X80 | 80 | 420
68 | Kalwa
69 | Karad |  |  | MSETCL | 1X80 | 80 | 420
70 | Kasor |  |  | GETCO | 1X50 + 1X125 | 175 | 420
71 | Katni
72 | Khandwa |  |  | PGCIL | 2X125 | 250 | 420
73 | Khaparkheda
74 | Kharghar |  |  | MSETCL | 1X80 | 80 | 420
75 | Kolhapur |  |  | MSETCL | 1X80 | 80 | 420
76 | Kolhapur-PG |  |  | PGCIL | 1x125 | 125 | 420
77 | Koradi |  |  | MSETCL | 1X50 | 50 | 420
78 | Koradi-II
79 | Korba (W)
80 | Korba (W)-Ext
81 | Korba-NTPC
82 | Kosamba |  |  | GETCO | 1X80 | 80 | 420
83 | Koyna stage-IV
84 | KSK Mahanadi
85 | KWPCL
86 | Lara |  |  | NTPC
87 | Lonikhand |  |  | MSETCL | 1X50 | 50 | 420
88 | Lonikhand-II
89 | Magarawada |  |  | PGCIL | 1x80 | 80 | 420
90 | Malwa
91 | Mansar |  |  | GETCO | 1x63 | 63 | 420
92 | Mapusa |  |  | PGCIL | 1X50 | 50 | 420
93 | Marwa
94 | MB Power |  |  | MB Power | 1x125 | 125 | 420
95 | MCCPL
96 | Mouda |  |  | NTPC | 1x80 | 80 | 420
97 | Nagda |  |  | MPPTCL | 2X50 | 100 | 420
98 | Nagothane |  |  | MSETCL | 1X80 | 80 | 420
99 | Nanded |  |  | MSETCL
100 | Nandgaonpeth |  |  | Rattan India | 1x80 | 80 | 420
101 | Navsari |  |  | PGCIL | 1X63 | 63 | 420
102 | New koyna
103 | NSPCL
104 | Padghe |  |  | MSETCL | 1X80 | 80 | 420
105 | Parli-M |  |  | MSETCL | 1X50 | 50 | 420
106 | Parli-PG |  |  | PGCIL | 1X63 + 1X125 | 188 | 420
107 | Pathadi
108 | Pirana-PG |  |  | PGCIL | 1X125 | 125 | 420
109 | Pirana-T
110 | Pithampur |  |  | MPPTCL | 1x50 | 50 | 420
111 | Pune-PG |  |  | PGCIL | 1X50 | 50 | 420
112 | Pune-PG(Shikrapur)
113 | Raigarh |  |  | PGCIL | 1X63 + 1X125 | 188 | 420
114 | Raigarh-PS(Kotra) |  |  | PGCIL | 1X80 | 80 | 420
115 | Raipur |  |  | PGCIL | 1X125 + 1X80 | 205 | 420
116 | Raipur-PS(Durg)
117 | Raita
118 | Rajgarh |  |  | PGCIL | 1X125 | 125 | 420
119 | Ranchodpura |  |  | GETCO | 1X50 + 1X125 | 175 | 420
120 | RGPPL
121 | RKM |  |  | RKM | 2x50 | 100 | 420
122 | Sami |  |  | APL | 1X50 | 50 | 420
123 | Sasan
124 | Satna |  |  | PGCIL | 1X50 + 1X63 | 113 | 420
125 | Satpura |  |  | MPPTCL | 2X63 | 126 | 420
126 | Seoni |  |  | PGCIL | 2x125 | 250 | 420
127 | Sholapur-M
128 | Shujalpur |  |  | PGCIL | 1X63 + 1X125 | 188 | 420
129 | Sipat
130 | SKS |  |  | SPGCL | 1x50 | 50 | 420
131 | Soja |  |  | GETCO | 1X50 + 1X80 | 130 | 420
132 | Solapur-NTPC
133 | Solapur-PG |  |  | PGCIL | 1X63 | 63 | 420
134 | SSP
135 | Sugen
136 | Tamnar
137 | Taptithanda
138 | Tarapur-3&4
139 | Tiroda |  |  | MEGPTCL | 2X80 | 160 | 420
140 | TRN
141 | Ukai
142 | Uno-Sugen |  |  | TPL | 1x80 | 80 | 420
143 | Vadinar
144 | Vadodara-PS
145 | Vandana
146 | Vapi
147 | Varsana |  |  | GETCO | 1X50 + 1X125 | 175 | 420
148 | Vindhyachal |  |  | NTPC | 1X63 + 1X50 | 113 | 420
149 | Vindhyachal-III
150 | Vindhyachal-IV |  |  | NTPC | 1X80 | 80 | 420
151 | Vindhyachal-PS |  |  | PGCIL | 1X63 | 63 | 420
152 | Vindhyachal-V |  |  | NTPC | 1x125 | 125 | 420
153 | Wanakbori
154 | Wardha |  |  | PGCIL | 1X50 | 50 | 420
155 | Warora |  |  | ATIL | 1x125 | 125 | 420
156 | Zerda(Kansari) |  |  | GETCO | 1X50 + 1x125 | 175 | 420

## 400kV Lines
Sl No | End-1 | End-2 | Id | Line Owner | End-1 Owner | End-2 Owner | Km | Conductor Type | SIL | No Load MVAR Generated | End1 LR |  | End2 LR | [6 empty] | End-1 | [5 empty] | End-2
[11 empty] | MVAR | S/W | MVAR | S/W | [5 empty] | 50 MVAR SLR | 50 MVAR NSLR | 63 MVAR SLR | 63 MVAR NSLR | 80 MVAR SLR | 80 MVAR NSLR | 50 MVAR SLR | 50 MVAR NSLR | 63 MVAR SLR | 63 MVAR NSLR | 80 MVAR SLR | 80 MVAR NSLR
1 | ACBIL | Bilaspur | 1 | WRTS-1 | ACBIL | WRTS-1 | 56 | Twin ACSR Moose | 517.1749 | 31.08 | - | - | - | - |  | X | B | Zpu | Z(ohms) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2 | ACBIL | MCCPL | 1 | WRTS-1 | ACBIL | MCCPL | 16 | Twin ACSR Moose | 517.1749 | 8.88 | - | - | - | - | Twin ACSR Moose | 0.0002075 | 0.00555 | 0.19336 | 309.3731 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
3 | Akola | Aurangabad-PG | 1 | MSETCL | WRTS-1 | WRTS-1 | 178 | Twin ACSR Moose | 517.1749 | 98.79 | 50 | - | 50 | - | Quad AAAC Moose | 0.0001676 | 0.00693 | 0.15551 | 248.8229 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0
4 | Akola | Aurangabad-PG | 2 | MSETCL | WRTS-1 | WRTS-1 | 178 | Twin ACSR Moose | 517.1749 | 98.79 | 50 | - | 50 | - | Quad ACSR Moose | 0.000158 | 0.00732 | 0.14692 | 235.0677 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0
5 | Akola | Nandgaonpeth | 1 | MSETCL | MSETCL | Ratan India | 117 | Twin ACSR Moose | 517.1749 | 64.935 | - | - | - | - | Triple ACSR Snowbird | 0.0001718 | 0.00673 | 0.15977 | 255.6372 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
6 | Akola | Akola(2) | 1 | MEGPTL | MSETCL | MEGPTL | 30 | Twin ACSR Moose | 517.1749 | 16.65 | - | - | - | - | Quad Bersimis | 0.000156 | 0.00746 | 0.14461 | 231.3731 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
7 | Akola | Akola(2) | 2 | MEGPTL | MSETCL | MEGPTL | 30 | Twin ACSR Moose | 517.1749 | 16.65 | - | - | - | - | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
8 | Akola(2) | Nandgaonpeth | 1 | MEGPTL | MEGPTL | Ratan India | 104 | Twin ACSR Moose | 517.1749 | 57.72 | - | - | - | - | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
9 | Akola(2) | Nandgaonpeth | 2 | MEGPTL | MEGPTL | Ratan India | 104 | Twin ACSR Moose | 517.1749 | 57.72 | - | - | - | - | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
10 | Amreli | Hadala | 1 | GETCO | GETCO | GETCO | 165 | Twin ACSR Moose | 517.1749 | 91.575 | - | - | - | - | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
11 | Amreli | Chorania | 1 | GETCO | GETCO | GETCO | 164 | Twin ACSR Moose | 517.1749 | 91.02 | - | - | - | - | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
12 | Amreli | Jetpur | 1 | GETCO | GETCO | GETCO | 96 | Twin ACSR Moose | 517.1749 | 53.28 | - | - | - | - | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
13 | Amreli | Jetpur | 2 | GETCO | GETCO | GETCO | 96 | Twin ACSR Moose | 517.1749 | 53.28 | - | - | - | - | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
14 | APL-Mundra | Sami | 1 | ATIL | APL | ATIL | 282 | Twin ACSR Moose | 517.1749 | 156.51 | - | - | 50 | - | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0
15 | APL-Mundra | Sami | 2 | ATIL | APL | ATIL | 282 | Twin ACSR Moose | 517.1749 | 156.51 | - | - | 50 | - | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0
16 | APL-Mundra | Hadala | 1 | GETCO | GETCO | GETCO | 233 | Twin ACSR Moose | 517.1749 | 129.315 | - | - | 63 | - | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0
17 | APL-Mundra | Varsana | 1 | GETCO | APL | GETCO | 84 | Twin ACSR Moose | 517.1749 | 46.62 | - | - | - | - | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
18 | APL-Mundra | Varsana | 2 | GETCO | APL | GETCO | 84 | Twin ACSR Moose | 517.1749 | 46.62 | - | - | - | - | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
19 | APL-Mundra | Zerda(Kansari) | 1 | GETCO | APL | GETCO | 332 | Twin ACSR Moose | 517.1749 | 184.26 | - | - | 63 | - | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0
20 | Asoj | Chorania | 1 | GETCO | GETCO | GETCO | 177 | Twin ACSR Moose | 517.1749 | 98.235 | - | - | - | - | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
21 | Asoj | Chorania | 2 | GETCO | GETCO | GETCO | 166 | Twin ACSR Moose | 517.1749 | 92.13 | 50 | - | - | - | [5 empty] | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
22 | Asoj | Kosamba | 1 | GETCO | GETCO | GETCO | 122 | Twin ACSR Moose | 517.1749 | 67.71 | - | - | - | - | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
23 | Asoj | Wanakbori | 1 | GETCO | GETCO | GETCO | 76 | Twin ACSR Moose | 517.1749 | 42.18 | - | - | - | - | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
24 | Athena | Raigarh-PS(Kotra) | 1 | ACPL | ACPL | WRTS-1 | 25 | Quad ACSR Moose | 680.6549 | 18.3 | - | - | - | - | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
25 | Athena | Raigarh-PS(Kotra) | 2 | ACPL | ACPL | WRTS-1 | 25 | Quad ACSR Moose | 680.6549 | 18.3 | - | - | - | - | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
26 | Aurangabad-M(Waluj) | Pune-PG(Shikrapur) | 1 | WRTMPL | MSETCL | WRTS-1 | 315 | Twin ACSR Moose | 517.1749 | 174.825 | 50 | - | 50 | Yes | [5 empty] | 0 | 1 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0
27 | Aurangabad-M(Waluj) | Pune-PG(Shikrapur) | 2 | WRTMPL | MSETCL | WRTS-1 | 315 | Twin ACSR Moose | 517.1749 | 174.825 | 50 | - | 50 | Yes | [5 empty] | 0 | 1 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0
28 | Aurangabad-M(Waluj) | Aurangabad-PG | 1 | WRTS-1 | MSETCL | WRTS-1 | 54 | Quad ACSR Moose | 680.6549 | 39.528 | - | - | - | - | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
29 | Aurangabad-M(Waluj) | Aurangabad-PG | 2 | WRTS-1 | MSETCL | WRTS-1 | 54 | Quad ACSR Moose | 680.6549 | 39.528 | - | - | - | - | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
30 | Aurangabad-M(Waluj) | Taptithanda | 1 | MSETCL | MSETCL | MSETCL | 135 | Twin ACSR Moose | 517.1749 | 74.925 | - | - | - | - | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
31 | Aurangabad-M(Waluj) | Deepnagar | 2 | MSETCL | MSETCL | MSETCL | 185 | Twin ACSR Moose | 517.1749 | 102.675 | - | - | - | - | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
32 | Aurangabad-PG | Boisar | 1 | WRTS-1 | WRTS-1 | WRTS-1 | 327 | Twin ACSR Moose | 517.1749 | 181.485 | 80 | Yes | 80 | - | [5 empty] | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 1
33 | Aurangabad-PG | Boisar | 2 | WRTS-1 | WRTS-1 | WRTS-1 | 327 | Twin ACSR Moose | 517.1749 | 181.485 | 80 | Yes | 80 | - | [5 empty] | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 1
34 | Bableshwar | Padghe | 1 | MSETCL | MSETCL | MSETCL | 174 | Twin ACSR Moose | 517.1749 | 96.57 | - | - | - | - | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
35 | Bableshwar | Padghe | 2 | MSETCL | MSETCL | MSETCL | 174 | Twin ACSR Moose | 517.1749 | 96.57 | - | - | - | - | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
36 | Bableshwar | Aurangabad-M(Waluj) | 1 | MSETCL | MSETCL | MSETCL | 131 | Twin ACSR Moose | 517.1749 | 72.705 | - | - | - | - | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
37 | Bableshwar | IB-Nasik | 1 | MSETCL | MSETCL | Ratan India | 72 | Twin ACSR Moose | 517.1749 | 39.96 | - | - | - | - | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
38 | Bableshwar | IB-Nasik | 2 | MSETCL | MSETCL | Ratan India | 72 | Twin ACSR Moose | 517.1749 | 39.96 | - | - | - | - | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
39 | Bachau | Ranchodpura | 1 | WRTS-2 | WRTS-2 | GETCO | 282 | Triple ACSR Snowbird | 625.887 | 189.786 | - | - | 50 | - | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0
40 | Bachau | Ranchodpura | 2 | WRTS-2 | WRTS-2 | GETCO | 282 | Triple ACSR Snowbird | 625.887 | 189.786 | - | - | 50 | - | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0
41 | Bachau | Varsana | 1 | WRTS-2 | WRTS-2 | GETCO | 10 | Twin ACSR Moose | 517.1749 | 5.55 | - | - | - | - | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
42 | Bachau | Varsana | 2 | WRTS-2 | WRTS-2 | GETCO | 10 | Twin ACSR Moose | 517.1749 | 5.55 | - | - | - | - | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
43 | Bhadrawati | Bhilai | 1 | WRTS-1 | WRTS-1 | CSPTCL | 322 | Twin ACSR Moose | 517.1749 | 178.71 | 50 | - | 80 | - | [5 empty] | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1
44 | Bhadrawati | Raipur | 1 | WRTS-1 | WRTS-1 | WRTS-1 | 333 | Twin ACSR Moose | 517.1749 | 184.815 | 50 | - | 80 | - | [5 empty] | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1
45 | Bhadrawati | Raipur | 2 | WRTS-1 | WRTS-1 | WRTS-1 | 346 | Twin ACSR Moose | 517.1749 | 192.03 | 63 | - | 50 | Yes | [5 empty] | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0
46 | Bhadrawati | Raipur | 3 | WRTS-1 | WRTS-1 | WRTS-1 | 346 | Twin ACSR Moose | 517.1749 | 192.03 | 63 | - | 63 | - | [5 empty] | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0
47 | Bhadrawati | EMCO | 1 | GMR-EMCO | WRTS-1 | GMR-EMCO | 28 | Twin ACSR Moose | 517.1749 | 15.54 | - | - | - | - | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
48 | Bhadrawati | EMCO | 2 | GMR-EMCO | WRTS-1 | GMR-EMCO | 28 | Twin ACSR Moose | 517.1749 | 15.54 | - | - | - | - | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
49 | Bhadrawati | Parli-PG | 1 | WRTS-1 | WRTS-1 | WRTS-1 | 388 | Twin ACSR Moose | 517.1749 | 215.34 | 63 | - | 63 | - | [5 empty] | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0
50 | Bhadrawati | Dhariwal | 1 | WRTS-1 | WRTS-1 | Dhariwal Infra | 15 | Twin ACSR Moose | 517.1749 | 8.325 | 63 | - | - | - | [5 empty] | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
51 | Bhadrawati HVDC | Ramagundam | 1 | SRTS-1 | WRTS-1 | SRTS-1 | 178 | Twin ACSR Moose | 517.1749 | 98.79 | 50 | - | - | - | [5 empty] | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
52 | Bhadrawati HVDC | Ramagundam | 2 | SRTS-1 | WRTS-1 | SRTS-1 | 178 | Twin ACSR Moose | 517.1749 | 98.79 | 50 | - | - | - | [5 empty] | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
53 | Bhilai | Raipur | 1 | WRTS-1 | CSPTCL | WRTS-1 | 13 | Twin ACSR Moose | 517.1749 | 7.215 | - | - | - | - | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
54 | Bhilai | Seoni | 1 | WRTS-1 | CSPTCL | WRTS-1 | 230 | Twin ACSR Moose | 517.1749 | 127.65 | 50 | - | - | - | [5 empty] | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
55 | Bhilai | Bhatapara | 1 | WRTS-1 | CSPTCL | WRTS-1 | 93 | Twin ACSR Moose | 517.1749 | 51.615 | - | - | 50 | - | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0
56 | Bhilai | Raita | 1 | CSPTCL | CSPTCL | CSPTCL | 56 | Twin ACSR Moose | 517.1749 | 31.08 | - | - | - | - | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
57 | Bhilai | Raita | 2 | CSPTCL | CSPTCL | CSPTCL | 56 | Twin ACSR Moose | 517.1749 | 31.08 | - | - | - | - | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
58 | Bhilai | Raita | 3 | CSPTCL | CSPTCL | CSPTCL | 56 | Twin ACSR Moose | 517.1749 | 31.08 | - | - | - | - | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
59 | Bhopal-BDTCL | Bhopal-MP | 1 | BDTCL | BDTCL | MPPTCL | 9 | Twin ACSR Moose | 517.1749 | 4.995 | - | - | - | - | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
60 | Bhopal-BDTCL | Bhopal-MP | 2 | BDTCL | BDTCL | MPPTCL | 9 | Twin ACSR Moose | 517.1749 | 4.995 | - | - | - | - | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
61 | Bhopal-MP | Bina-MP | 1 | MPPTCL | MPPTCL | MPPTCL | 289 | Twin ACSR Moose | 517.1749 | 160.395 | - | - | 50 | - | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0
62 | Bhopal-MP | Bina-MP | 2 | MPPTCL | MPPTCL | MPPTCL | 273 | Twin ACSR Moose | 517.1749 | 151.515 | - | - | 50 | - | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0
63 | Bhopal-MP | Itarsi | 1 | MPPTCL | MPPTCL | WRST-2 | 98 | Twin ACSR Moose | 517.1749 | 54.39 | - | - | - | - | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
64 | Bhopal-MP | Itarsi | 2 | MPPTCL | MPPTCL | WRST-2 | 98 | Twin ACSR Moose | 517.1749 | 54.39 | - | - | - | - | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
65 | Bhopal-MP | Damoh | 1 | WRTS-2 | MPPTCL | WRST-2 | 214 | Twin ACSR Moose | 517.1749 | 118.77 | 50 | - | - | - | [5 empty] | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
66 | Bhopal-MP | Damoh | 2 | WRTS-2 | MPPTCL | WRST-2 | 214 | Twin ACSR Moose | 517.1749 | 118.77 | 50 | - | - | - | [5 empty] | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
67 | Bhusawal (Khadka) | Bableshwar | 1 | MSETCL | MSETCL | MSETCL | 220 | Twin ACSR Moose | 517.1749 | 122.1 | - | - | - | - | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
68 | Bhusawal (Khadka) | Aurangabad-M(Waluj) | 1 | MSETCL | MSETCL | MSETCL | 238 | Twin ACSR Moose | 517.1749 | 132.09 | - | - | 50 | - | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0
69 | Bhusawal (Khadka) | Akola | 1 | MSETCL | MSETCL | MSETCL | 182 | Twin ACSR Moose | 517.1749 | 101.01 | 50 | - | - | - | [5 empty] | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
70 | Bhusawal (Khadka) | Deepnagar | 1 | MSETCL | MSETCL | MSETCL | 15 | Twin ACSR Moose | 517.1749 | 8.325 | - | - | - | - | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
71 | Bhusawal (Khadka) | Deepnagar | 2 | MSETCL | MSETCL | MSETCL | 15 | Twin ACSR Moose | 517.1749 | 8.325 | - | - | - | - | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
72 | Bina-MP | JP-Bina | 1 | MPPTCL | MPPTCL | Jaypee | 20 | Twin ACSR Moose | 517.1749 | 11.1 | - | - | - | - | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
73 | Bina-MP | Bina-PG | 1 | WRTS-2 | MPPTCL | WRST-2 | 3 | Twin ACSR Moose | 517.1749 | 1.665 | - | - | - | - | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
74 | Bina-MP | Bina-PG | 2 | WRTS-2 | MPPTCL | WRST-2 | 3 | Twin ACSR Moose | 517.1749 | 1.665 | - | - | - | - | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
75 | Bina-MP | Bina-PG | 3 | WRTS-2 | MPPTCL | WRST-2 | 3 | Twin ACSR Moose | 517.1749 | 1.665 | - | - | - | - | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
76 | Bina-MP | Bina-PG | 4 | WRTS-2 | MPPTCL | WRST-2 | 3 | Twin ACSR Moose | 517.1749 | 1.665 | - | - | - | - | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
77 | Bina-PG | Shujalpur | 1 | WRTS-2 | WRST-2 | WRST-2 | 200 | Twin ACSR Moose | 517.1749 | 111 | 63 | Yes | 50 | - | [5 empty] | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0
78 | Bina-PG | Shujalpur | 2 | WRTS-2 | WRST-2 | WRST-2 | 200 | Twin ACSR Moose | 517.1749 | 111 | 63 | Yes | 50 | - | [5 empty] | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0
79 | Bina-PG | JP-Bina | 1 | WRTS-2 | WRTS-2 | Jaypee | 20 | Twin ACSR Moose | 517.1749 | 11.1 | - | - | - | - | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
80 | Bina-PG | Bina-NTS | 1 | WRTS-2 | WRTS-2 | NHPTL | 1 | Twin ACSR Moose | 517.1749 | 0.555 | 50 | - | - | - | [5 empty] | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
81 | Bina-PG | NHPTL | 1 | WRTS-2 | WRTS-2 | NHPTL | 0.4 | Twin ACSR Moose | 517.1749 | 0.222 | - | - | - | -
82 | Birsingpur | Katni | 1 | MPPTCL | MPPTCL | MPPTCL | 118 | Twin ACSR Moose | 517.1749 | 65.49 | - | - | - | - | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
83 | Birsingpur | Katni | 2 | MPPTCL | MPPTCL | MPPTCL | 118 | Twin ACSR Moose | 517.1749 | 65.49 | 63 | - | - | - | [5 empty] | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
84 | Birsingpur | Vandana | 1 | WRTS-2 | MPPTCL | Vandana Vidyut | 215 | Twin ACSR Moose | 517.1749 | 119.325 | - | - | 50 | - | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0
85 | CGPL | Chorania | 1 | WRTS-2 | CGPL | GETCO | 314 | Triple ACSR Snowbird | 625.887 | 211.322 | 63 | Yes | 63 | - | [5 empty] | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0
86 | CGPL | Mansar | 1 | WRTS-2 | CGPL | GETCO | 224 | Triple ACSR Snowbird | 625.887 | 150.752 | 63 | Yes | - | - | [5 empty] | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
87 | CGPL | Jetpur | 1 | WRTS-2 | CGPL | GETCO | 334 | Triple ACSR Snowbird | 625.887 | 224.782 | 63 | Yes | 63 | - | [5 empty] | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0
88 | CGPL | Jetpur | 2 | WRTS-2 | CGPL | GETCO | 334 | Triple ACSR Snowbird | 625.887 | 224.782 | 63 | Yes | 63 | - | [5 empty] | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0
89 | CGPL | Bachau | 1 | WRTS-2 | CGPL | WRTS-2 | 100 | Triple ACSR Snowbird | 625.887 | 67.3 | - | - | - | - | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
90 | CGPL | Bachau | 2 | WRTS-2 | CGPL | WRTS-2 | 100 | Triple ACSR Snowbird | 625.887 | 67.3 | - | - | - | - | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
91 | Chakan | Pune-PG | 1 | WRTS-1 | MSETCL | WRTS-1 | 18 | Twin ACSR Moose | 517.1749 | 9.99 | - | - | - | - | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
92 | Chandrapur | Bhadrawati | 1 | WRTS-1 | MSETCL | WRTS-1 | 20 | Twin ACSR Moose | 517.1749 | 11.1 | - | - | - | - | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
93 | Chandrapur | Bhadrawati | 2 | WRTS-1 | MSETCL | WRTS-1 | 20 | Twin ACSR Moose | 517.1749 | 11.1 | - | - | - | - | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
94 | Chandrapur | Bhadrawati | 3 | WRTS-1 | MSETCL | WRTS-1 | 22 | Twin ACSR Moose | 517.1749 | 12.21 | - | - | - | - | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
95 | Chandrapur | Bhadrawati | 4 | WRTS-1 | MSETCL | WRTS-1 | 22 | Twin ACSR Moose | 517.1749 | 12.21 | - | - | - | - | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
96 | Chandrapur | Khaparkheda | 1 | MSETCL | MSETCL | MSETCL | 156 | Twin ACSR Moose | 517.1749 | 86.58 | - | - | - | - | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
97 | Chandrapur | Chandrapur-II | 1 | MSETCL | MSETCL | MSETCL | 1 | Twin ACSR Moose | 517.1749 | 0.555 | 50 | - | - | - | [5 empty] | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
98 | Chandrapur | Chandrapur-II | 2 | MSETCL | MSETCL | MSETCL | 1 | Twin ACSR Moose | 517.1749 | 0.555 | 50 | - | - | - | [5 empty] | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
99 | Chandrapur | Parli-M | 3 | MSETCL | MSETCL | MSETCL | 371 | Twin ACSR Moose | 517.1749 | 205.905 | 50 | - | 50 | - | [5 empty] | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0
100 | Chandrapur-II | Dhariwal | 1 | MSETCL | MSETCL | Dhariwal Infra | 8 | Twin ACSR Moose | 517.1749 | 4.44 | - | - | - | - | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
101 | Chandrapur-II | Dhariwal | 2 | MSETCL | MSETCL | Dhariwal Infra | 8 | Twin ACSR Moose | 517.1749 | 4.44 | - | - | - | - | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
102 | Chandrapur-II | Nanded | 1 | MSETCL | MSETCL | MSETCL | 257 | Twin ACSR Moose |  |  | - | - | - | - | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
103 | Chhegaon | Julwania | 1 | MPPTCL | MPPTCL | MPPTCL | 114 | Twin ACSR Moose | 517.1749 | 63.27 | - | - | - | - | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
104 | Chorania | Kosamba | 1 | GETCO | GETCO | GETCO | 230 | Twin ACSR Moose | 517.1749 | 127.65 | 50 | - | 63 | - | [5 empty] | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0
105 | Chorania | Kosamba | 2 | GETCO | GETCO | GETCO | 230 | Twin ACSR Moose | 517.1749 | 127.65 | 50 | - | 63 | - | [5 empty] | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0
106 | Damoh | Birsingpur | 1 | WRTS-2 | WRTS-2 | MPPTCL | 227 | Twin ACSR Moose | 517.1749 | 125.985 | 50 | - | - | - | [5 empty] | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
107 | Damoh | Birsingpur | 2 | WRTS-2 | WRTS-2 | MPPTCL | 227 | Twin ACSR Moose | 517.1749 | 125.985 | 50 | - | - | - | [5 empty] | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
108 | Damoh | Katni | 1 | MPPTCL | WRTS-2 | MPPTCL | 118 | Twin ACSR Moose | 517.1749 | 65.49 | 50 | - | - | - | [5 empty] | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
109 | DB-Power | Raigarh-PS(Kotra) | 1 | DB-Power | DB-Power | WRTS-1 | 18 | Twin ACSR Moose | 517.1749 | 9.99 | - | - | - | - | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
110 | DB-Power | Raigarh-PS(Kotra) | 2 | DB-Power | DB-Power | WRTS-1 | 18 | Twin ACSR Moose | 517.1749 | 9.99 | - | - | - | - | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
111 | Dehgam | Gandhar | 1 | WRTS-2 | WRTS-2 | NTPC | 157 | Twin ACSR Moose | 517.1749 | 87.135 | - | - | - | - | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
112 | Dehgam | Gandhar | 2 | WRTS-2 | WRTS-2 | NTPC | 157 | Twin ACSR Moose | 517.1749 | 87.135 | - | - | - | - | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
113 | Dehgam | Pirana-PG | 1 | WRTS-2 | WRTS-2 | WRTS-2 | 56 | Twin ACSR Moose | 517.1749 | 31.08 | - | - | - | - | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
114 | Dehgam | Pirana-PG | 2 | WRTS-2 | WRTS-2 | WRTS-2 | 56 | Twin ACSR Moose | 517.1749 | 31.08 | - | - | - | - | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
115 | Dehgam | Sami | 1 | ATIL | WRTS-2 | ATIL | 152 | Twin ACSR Moose | 517.1749 | 84.36 | - | - | - | - | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
116 | Dehgam | Sami | 2 | ATIL | WRTS-2 | ATIL | 152 | Twin ACSR Moose | 517.1749 | 84.36 | - | - | - | - | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
117 | Dehgam | Ranchodpura | 1 | GETCO | WRTS-2 | GETCO | 62 | Twin ACSR Moose | 517.1749 | 34.41 | - | - | - | - | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
118 | Dehgam | Ranchodpura | 2 | GETCO | WRTS-2 | GETCO | 62 | Twin ACSR Moose | 517.1749 | 34.41 | - | - | - | - | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
119 | Dehgam | Wanakbori | 1 | WRTS-2 | WRTS-2 | GETCO | 68 | Twin ACSR Moose | 517.1749 | 37.74 | - | - | - | - | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
120 | Dharamjaygarh | Balco | 1 | BALCO | WRTS-1 | BALCO | 23.2 | Twin ACSR Moose | 517.1749 | 12.876 | - | - | - | - | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
121 | Dharamjaygarh | Balco | 2 | BALCO | WRTS-2 | BALCO | 23.2 | Twin ACSR Moose | 517.1749 | 12.876 | - | - | - | - | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
122 | Dhariwal | Parli-PG | 1 | WRTS-1 | Dhariwal Infra | WRTS-1 | 390 | Twin ACSR Moose | 517.1749 | 216.45 | - | - | 63 | - | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0
123 | Dhule-BDTCL | Dhule-MS | 1 | BDTCL | BDTCL | MSETCL | 18 | Twin ACSR Moose | 517.1749 | 9.99 | - | - | - | - | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
124 | Dhule-BDTCL | Dhule-MS | 2 | BDTCL | BDTCL | MSETCL | 18 | Twin ACSR Moose | 517.1749 | 9.99 | - | - | - | - | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
125 | Dhule-MS | Bableshwar | 1 | MSETCL | MSETCL | MSETCL | 170 | Twin ACSR Moose | 517.1749 | 94.35 | - | - | - | - | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
126 | Dhule-MS | Bableshwar | 2 | MSETCL | MSETCL | MSETCL | 170 | Twin ACSR Moose | 517.1749 | 94.35 | - | - | - | - | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
127 | Ektuni (Aurangabad(3)) | Bableshwar | 1 | MSETCL | MSETCL | MSETCL | 127 | Quad ACSR Moose | 680.6549 | 92.964 | - | - | - | - | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
128 | Ektuni (Aurangabad(3)) | Bableshwar | 2 | MSETCL | MSETCL | MSETCL | 127 | Quad ACSR Moose | 680.6549 | 92.964 | - | - | - | - | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
129 | Gandhar | Navsari | 1 | WRTS-2 | NTPC | WRTS-2 | 106 | Twin ACSR Moose | 517.1749 | 58.83 | - | - | - | - | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
130 | Gandhar | Kosamba | 1 | WRTS-2 | NTPC | GETCO | 93 | Twin ACSR Moose | 517.1749 | 51.615 | - | - | - | - | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
131 | Gandhar | Hazira | 1 | EPTCL | NTPC | HAZIRA-IPP | 97 | Twin ACSR Moose | 517.1749 | 53.835 | - | - | - | - | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
132 | Gandhar | Hazira | 2 | EPTCL | NTPC | HAZIRA-IPP | 97 | Twin ACSR Moose | 517.1749 | 53.835 | - | - | - | - | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
133 | Gandhar | GPEC | 1 | GETCO | NTPC | GPEC | 13 | Twin ACSR Moose | 517.1749 | 7.215 | - | - | - | - | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
134 | Gandhar | Sugen | 1 | WRTS-2 | NTPC | TPL | 64 | Twin ACSR Moose | 517.1749 | 35.52 | 50 | - | - | - | [5 empty] | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
135 | GPEC | Kasor | 1 | GPEC | GPEC | GETCO | 98 | Twin ACSR Moose | 517.1749 | 54.39 | - | - | - | - | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
136 | Hadala | Varsana | 1 | GETCO | GETCO | GETCO | 159 | Twin ACSR Moose | 517.1749 | 88.245 | - | - | - | - | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
137 | Hadala | Vadinar | 1 | GETCO | GETCO | ESSAR | 113 | Twin ACSR Moose | 517.1749 | 62.715 | - | - | - | - | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
138 | Hadala | Vadinar | 2 | GETCO | GETCO | ESSAR | 113 | Twin ACSR Moose | 517.1749 | 62.715 | - | - | - | - | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
139 | Hadala | Chorania | 1 | GETCO | GETCO | GETCO | 166 | Twin ACSR Moose | 517.1749 | 92.13 | - | - | - | - | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
140 | IEPL | Warora | 1 | WRTS-1 | IEPL | MEGPTL | 150 | Twin ACSR Moose | 517.1749 | 83.25 | - | - | - | - | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
141 | IEPL | Koradi-II | 2 | WRTS-1 | IEPL | MSETCL | 94 | Twin ACSR Moose | 517.1749 | 52.17 | - | - | - | - | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
142 | Indira Sagar | Indore-MP | 1 | MPPTCL | MPPTCL | MPPTCL | 79 | Quad ACSR Moose | 680.6549 | 57.828 | - | - | - | - | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
143 | Indira Sagar | Indore-MP | 2 | MPPTCL | MPPTCL | MPPTCL | 80 | Quad ACSR Moose | 680.6549 | 58.56 | - | - | 50 | - | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0
144 | Indira Sagar | Nagda | 1 | MPPTCL | MPPTCL | MPPTCL | 188 | Twin ACSR Moose | 517.1749 | 104.34 | - | - | - | - | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
145 | Indore-MP | Indore-PG | 1 | WRTS-2 | MPPTCL | WRTS-2 | 50 | Twin ACSR Moose | 517.1749 | 27.75 | - | - | - | - | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
146 | Indore-MP | Indore-PG | 2 | WRTS-2 | MPPTCL | WRTS-2 | 50 | Twin ACSR Moose | 517.1749 | 27.75 | - | - | - | - | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
147 | Indore-MP | Nagda | 1 | MPPTCL | MPPTCL | MPPTCL | 108 | Twin ACSR Moose | 517.1749 | 59.94 | - | - | - | - | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
148 | Indore-MP | Asoj | 1 | GETCO | MPPTCL | GETCO | 289 | Twin ACSR Moose | 517.1749 | 160.395 | 50 | - | 50 | - | [5 empty] | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0
149 | Indore-MP | Asoj | 2 | GETCO | MPPTCL | GETCO | 273 | Twin ACSR Moose | 517.1749 | 151.515 | 50 | - | 50 | - | [5 empty] | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0
150 | Indore-PG | Pithampur | 1 | MPPTCL | MPPTCL | MPPTCL | 150 | Twin ACSR Moose | 517.1749 | 83.25 | - | - | - | - | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
151 | Indore-PG | Pithampur | 2 | MPPTCL | MPPTCL | MPPTCL | 150 | Twin ACSR Moose | 517.1749 | 83.25 | - | - | - | - | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
152 | Itarsi | Indore-MP | 1 | WRTS-2 | WRTS-2 | MPPTCL | 207 | Twin ACSR Moose | 517.1749 | 114.885 | 50 | - | 50 | - | [5 empty] | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0
153 | Itarsi | Indore-MP | 2 | WRTS-2 | WRTS-2 | MPPTCL | 214 | Twin ACSR Moose | 517.1749 | 118.77 | 50 | - | 50 | - | [5 empty] | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0
154 | Itarsi | Khandwa | 1 | WRTS-2 | WRTS-2 | WRTS-2 | 197 | Twin ACSR Moose | 517.1749 | 109.335 | 50 | Yes | - | - | [5 empty] | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
155 | Itarsi | Khandwa | 2 | WRTS-2 | WRTS-2 | WRTS-2 | 197 | Twin ACSR Moose | 517.1749 | 109.335 | 50 | - | - | - | [5 empty] | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
156 | Jabalpur | Itarsi | 1 | WRTS-2 | WRTS-2 | WRTS-2 | 232 | Twin ACSR Moose | 517.1749 | 128.76 | 50 | - | 50 | - | [5 empty] | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0
157 | Jabalpur | Itarsi | 2 | WRTS-2 | WRTS-2 | WRTS-2 | 232 | Twin ACSR Moose | 517.1749 | 128.76 | 50 | - | 50 | - | [5 empty] | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0
158 | Jabalpur | Itarsi | 3 | WRTS-2 | WRTS-2 | WRTS-2 | 234 | Twin ACSR Moose | 517.1749 | 129.87 | 50 | Yes | 50 | - | [5 empty] | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0
159 | Jabalpur | Itarsi | 4 | WRTS-2 | WRTS-2 | WRTS-2 | 234 | Twin ACSR Moose | 517.1749 | 129.87 | 50 | Yes | 50 | - | [5 empty] | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0
160 | Jabalpur | Sasan | 1 | WRTS-2 | WRTS-2 | SPL | 340 | Twin ACSR Moose | 517.1749 | 188.7 | 63 | - | 50 | - | [5 empty] | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0
161 | Jabalpur | Jabalpur (PS) | 1 | WRTS-2 | WRTS-2 | WRTS-2 | 16 | Quad ACSR Moose | 680.6549 | 11.712 | - | - | - | - | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
162 | Jabalpur | Jabalpur (PS) | 2 | WRTS-2 | WRTS-2 | WRTS-2 | 16 | Quad ACSR Moose | 680.6549 | 11.712 | - | - | - | - | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
163 | Jabalpur (PS) | MB Power | 1 | WRTS-2 | WRTS-2 | MB-Power | 246 | Triple ACSR Snowbird | 625.887 | 165.558 | 50 | - | - | - | [5 empty] | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
164 | Jabalpur (PS) | MB Power | 2 | WRTS-2 | WRTS-2 | MB-Power | 246 | Triple ACSR Snowbird | 625.887 | 165.558 | 50 | - | - | - | [5 empty] | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
165 | Jabalpur (PS) | Jhabua Power | 1 | Jhabua Power Ltd | WRTS-2 | Jhabua Power | 65 | Twin ACSR Moose | 517.1749 | 36.075 | - | - | - | - | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
166 | Jabalpur (PS) | Jhabua Power | 2 | Jhabua Power Ltd | WRTS-2 | Jhabua Power | 65 | Twin ACSR Moose | 517.1749 | 36.075 | - | - | - | - | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
167 | Jaigad | New koyna | 1 | MSETCL | JAIGAD-IPP | MSETCL | 55 | Twin ACSR Moose | 517.1749 | 30.525 | - | - | - | - | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
168 | Jaigad | New koyna | 2 | MSETCL | JAIGAD-IPP | MSETCL | 55 | Twin ACSR Moose | 517.1749 | 30.525 | - | - | - | - | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
169 | Jejuri | Koyna stage-IV | 1 | MSETCL | MSETCL | MSETCL | 172 | Twin ACSR Moose | 517.1749 | 95.46 | - | - | - | - | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
170 | JPL | Raipur | 1 | JPL | JPL | WRTS-1 | 258 | Twin ACSR Moose | 517.1749 | 143.19 | - | - | 50 | - | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0
171 | JPL | Raipur | 2 | JPL | JPL | WRTS-1 | 258 | Twin ACSR Moose | 517.1749 | 143.19 | - | - | 50 | - | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0
172 | JPL | JPL_extn(Tamnar) | 1 | JPL | JPL | JPL | 2 | Twin ACSR Moose | 517.1749 | 1.11 | - | - | - | - | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
173 | JPL_extn(Tamnar) | Tamnar-PS | 1 | JPL | JPL | WRTS-1 | 10 | Twin ACSR Moose | 517.1749 | 5.55 | - | - | - | - | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
174 | JPL_extn(Tamnar) | Tamnar-PS | 2 | JPL | JPL | WRTS-1 | 10 | Twin ACSR Moose | 517.1749 | 5.55 | - | - | - | - | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
175 | JPL_extn(Tamnar) | Tamnar-PS | 4 | JPL | JPL | WRTS-1 | 10 | Twin ACSR Moose | 517.1749 | 5.55 | - | - | - | - | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
176 | JPL_extn(Tamnar) | Tamnar-PS | 3 | JPL | JPL | WRTS-1 | 10 | Twin ACSR Moose | 517.1749 | 5.55 | - | - | - | - | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
177 | Kala | Vapi | 1 | WRTS-2 | WRTS-2 | WRTS-2 | 49 | Twin ACSR Moose | 517.1749 | 27.195 | - | - | - | - | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
178 | Kala | Vapi | 2 | WRTS-2 | WRTS-2 | WRTS-2 | 52 | Twin ACSR Moose | 517.1749 | 28.86 | - | - | - | - | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
179 | Kalwa | Padghe | 1 | MSETCL | MSETCL | MSETCL | 72 | Twin ACSR Moose | 517.1749 | 39.96 | - | - | - | - | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
180 | Kalwa | Padghe | 2 | MSETCL | MSETCL | MSETCL | 72 | Twin ACSR Moose | 517.1749 | 39.96 | - | - | - | - | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
181 | Kalwa | Kharghar | 1 | MSETCL | MSETCL | MSETCL | 28 | Twin ACSR Moose | 517.1749 | 15.54 | - | - | - | - | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
182 | Kalwa | Pune-PG | 1 | MSETCL | MSETCL | WRTS-1 | 104 | Twin ACSR Moose | 517.1749 | 57.72 | - | - | - | - | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
183 | Karad | Kolhapur | 1 | MSETCL | MSETCL | MSETCL | 105 | Twin ACSR Moose | 517.1749 | 58.275 | - | - | - | - | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
184 | Karad | Kolhapur | 2 | MSETCL | MSETCL | MSETCL | 105 | Twin ACSR Moose | 517.1749 | 58.275 | - | - | - | - | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
185 | Karad | Jaigad | 1 | MSETCL | MSETCL | JAIGAD-IPP | 111 | Twin ACSR Moose | 517.1749 | 61.605 | - | - | - | - | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
186 | Karad | Jaigad | 2 | MSETCL | MSETCL | JAIGAD-IPP | 111 | Twin ACSR Moose | 517.1749 | 61.605 | - | - | - | - | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
187 | Karad | New Koyna | 1 | MSETCL | MSETCL | MSETCL | 72 | Twin ACSR Moose | 517.1749 | 39.96 | - | - | - | - | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
188 | Karad | New Koyna | 2 | MSETCL | MSETCL | MSETCL | 72 | Twin ACSR Moose | 517.1749 | 39.96 | - | - | - | - | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
189 | Karad | Solapur-PG | 1 | WRTMPL/MSETCL | MSETCL | WRTS-1 | 299 | Twin ACSR Moose | 517.1749 | 165.945 | 50 | - | 80 | Yes | [5 empty] | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0
190 | Karad | Lonikhand | 1 | MSETCL | MSETCL | MSETCL | 161 | Twin ACSR Moose | 517.1749 | 89.355 | 80 | - | - | - | [5 empty] | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0
191 | Kasor | Chorania | 1 | GETCO | GETCO | GETCO | 103 | Twin ACSR Moose | 517.1749 | 57.165 | - | - | - | - | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
192 | Khandwa | Dhule-MS | 1 | WRTS-2 | WRTS-2 | MSETCL | 262 | Twin ACSR Moose | 517.1749 | 145.41 | 50 | - | 50 | - | [5 empty] | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0
193 | Khandwa | Dhule-MS | 2 | WRTS-2 | WRTS-2 | MSETCL | 262 | Twin ACSR Moose | 517.1749 | 145.41 | 50 | - | 50 | - | [5 empty] | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0
194 | Khandwa | Rajgarh | 1 | WRTS-2 | WRTS-2 | WRTS-2 | 221 | Twin ACSR Moose | 517.1749 | 122.655 | - | - | - | - | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
195 | Khandwa | Rajgarh | 2 | WRTS-2 | WRTS-2 | WRTS-2 | 221 | Twin ACSR Moose | 517.1749 | 122.655 | - | - | - | - | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
196 | Kharghar | Padghe | 1 | MSETCL | MSETCL | MSETCL | 85 | Twin ACSR Moose | 517.1749 | 47.175 | - | - | - | - | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
197 | Kolhapur | Kolhapur-PG | 1 | WRTS-1 | MSETCL | WRTS-1 | 39 | Twin ACSR Moose | 517.1749 | 21.645 | - | - | - | - | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
198 | Kolhapur | Kolhapur-PG | 2 | WRTS-1 | MSETCL | WRTS-1 | 39 | Twin ACSR Moose | 517.1749 | 21.645 | - | - | - | - | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
199 | Kolhapur | Solapur-PG | 1 | WRTMPL | MSETCL | WRTS-1 | 220 | Twin ACSR Moose | 517.1749 | 122.1 | - | - | 50 | - | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0
200 | Kolhapur | Solapur-PG | 2 | WRTMPL | MSETCL | WRTS-1 | 220 | Twin ACSR Moose | 517.1749 | 122.1 | - | - | 50 | - | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0
201 | Kolhapur-PG | Mapusa | 1 | WRTS-1 | WRTS-1 | WRTS-1 | 156 | Twin ACSR Moose | 517.1749 | 86.58 | - | - | - | - | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
202 | Kolhapur-PG | Mapusa | 2 | WRTS-1 | WRTS-1 | WRTS-1 | 156 | Twin ACSR Moose | 517.1749 | 86.58 | - | - | - | - | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
203 | Koradi | Bhusawal (Khadka) | 2 | MSETCL | MSETCL | MSETCL | 343 | Twin ACSR Moose | 517.1749 | 190.365 | 50 | - | 50 | - | [5 empty] | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0
204 | Koradi | Satpura | 1 | WRTS-1 | MSETCL | MPPTCL | 149 | Twin ACSR Moose | 517.1749 | 82.695 | - | - | 50 | - | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0
205 | Koradi | Bhilai | 1 | WRTS-1 | MSETCL | CSPTCL | 272 | Twin ACSR Moose | 517.1749 | 150.96 | 50 | - | 50 | - | [5 empty] | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0
206 | Koradi | Khaparkheda | 1 | MSETCL | MSETCL | MSETCL | 10 | Twin ACSR Moose | 517.1749 | 5.55 | - | - | - | - | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
207 | Koradi | Khaparkheda | 2 | MSETCL | MSETCL | MSETCL | 10 | Twin ACSR Moose | 517.1749 | 5.55 | - | - | - | - | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
208 | Korba (W) | Korba-NTPC | 1 | WRTS-1 | CSPTCL | NTPC | 14 | Twin ACSR Moose | 517.1749 | 7.77 | - | - | - | - | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
209 | Korba (W) | Raita | 1 | CSPTCL | CSPTCL | CSPTCL | 144 | Twin ACSR Moose | 517.1749 | 79.92 | - | - | - | - | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
210 | Korba (W) | Korba (W)-Ext | 1 | CSPTCL | CSPTCL | CSPTCL | 1 | Twin ACSR Moose | 517.1749 | 0.555 | - | - | - | - | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
211 | Korba (W)-Ext | Bhilai | 1 | CSPTCL | CSPTCL | CSPTCL | 220 | Twin ACSR Moose | 517.1749 | 122.1 | - | - | 50 | - | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0
212 | Korba (W)-Ext | Marwa | 1 | CSPTCL | CSPTCL | CSPTCL | 60 | Twin ACSR Moose | 517.1749 | 33.3 | - | - | - | - | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
213 | Korba-NTPC | Bhilai | 1 | WRTS-1 | NTPC | CSPTCL | 197 | Twin ACSR Moose | 517.1749 | 109.335 | - | - | 50 | - | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0
214 | Korba-NTPC | Bhilai | 2 | WRTS-1 | NTPC | CSPTCL | 192 | Twin ACSR Moose | 517.1749 | 106.56 | - | - | 50 | - | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0
215 | Korba-NTPC | Raipur | 1 | WRTS-1 | NTPC | WRTS-1 | 212 | Twin ACSR Moose | 517.1749 | 117.66 | - | - | 63 | - | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0
216 | Korba-NTPC | Raipur | 2 | WRTS-1 | NTPC | WRTS-1 | 212 | Twin ACSR Moose | 517.1749 | 117.66 | - | - | 63 | - | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0
217 | Korba-NTPC | Sipat | 1 | WRTS-1 | NTPC | NTPC | 100 | Twin ACSR Moose | 517.1749 | 55.5 | - | - | - | - | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
218 | Korba-NTPC | Essar_Mahan | 1 | WRTS-1 | NTPC | ESSAR | 218 | Twin ACSR Moose | 517.1749 | 120.99 | - | - | - | - | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
219 | Korba-NTPC | Vindhyachal | 2 | WRTS-1 | NTPC | NTPC | 289 | Twin ACSR Moose | 517.1749 | 160.395 | - | - | 50 | - | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0
220 | Korba-NTPC | Bhatapara | 1 | WRTS-1 | NTPC | WRTS-1 | 124 | Twin ACSR Moose | 517.1749 | 68.82 | - | - | - | - | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
221 | Korba-NTPC | Birsingpur | 2 | WRTS-2 | NTPC | BALCO | 260 | Twin ACSR Moose | 517.1749 | 144.3 | 50 | - | 50 | - | [5 empty] | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0
222 | Korba-NTPC | Vandana | 1 | WRTS-2 | NTPC | Vandana Vidyut | 18 | Twin ACSR Moose | 517.1749 | 9.99 | 50 | - | - | - | [5 empty] | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
223 | Koyna stage-IV | Lonikhand | 1 | MSETCL | MSETCL | MSETCL | 183 | Twin ACSR Moose | 517.1749 | 101.565 | - | - | - | - | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
224 | Koyna stage-IV | New Koyna | 1 | MSETCL | MSETCL | MSETCL | 14 | Twin ACSR Moose | 517.1749 | 7.77 | - | - | - | - | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
225 | Koyna stage-IV | New Koyna | 2 | MSETCL | MSETCL | MSETCL | 14 | Twin ACSR Moose | 517.1749 | 7.77 | - | - | - | - | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
226 | KSK Mahanadi | Raipur | 1 | WRTS-1 | KSK | WRTS-1 | 147 | Twin ACSR Moose | 517.1749 | 81.585 | - | - | 50 | - | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0
227 | KSK Mahanadi | Raipur | 2 | WRTS-1 | KSK | WRTS-1 | 150 | Twin ACSR Moose | 517.1749 | 83.25 | - | - | 50 | - | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0
228 | KSK Mahanadi | RKM | 1 | WRTS-1 | KSK | RKMPPL | 104 | Twin ACSR Moose | 517.1749 | 57.72 | - | - | - | - | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
229 | KWPCL | Raigarh-PS(Kotra) | 1 | KWPCL | KWPCL | WRTS-1 | 19 | Twin ACSR Moose | 517.1749 | 10.545 | - | - | - | - | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
230 | KWPCL | Raigarh-PS(Kotra) | 2 | KWPCL | KWPCL | WRTS-1 | 19 | Twin ACSR Moose | 517.1749 | 10.545 | - | - | - | - | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
231 | Lara | Raigarh-PS(Kotra) | 1 | WRTS-1 | NTPC | WRTS-1 | 18 | Twin ACSR Moose | 517.1749 | 9.99 | - | - | - | - | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
232 | Lara | Raigarh-PS(Kotra) | 2 | WRTS-1 | NTPC | WRTS-1 | 18 | Twin ACSR Moose | 517.1749 | 9.99 | - | - | - | - | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
233 | Lonikhand | Jejuri | 1 | MSETCL | MSETCL | MSETCL | 48 | Twin ACSR Moose | 517.1749 | 26.64 | - | - | - | - | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
234 | Lonikhand | Chakan | 1 | MSETCL | MSETCL | MSETCL | 37 | Twin ACSR Moose | 517.1749 | 20.535 | 50 | - | - | - | [5 empty] | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
235 | Lonikhand | Pune-PG | 1 | MSETCL | MSETCL | WRTS-1 | 40 | Twin ACSR Moose | 517.1749 | 22.2 | - | - | - | - | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
236 | Lonikhand-II | Lonikhand | 1 | MSETCL | MSETCL | MSETCL | 1 | Twin ACSR Moose | 517.1749 | 0.555 | - | - | - | - | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
237 | Lonikhand-II | Lonikhand | 2 | MSETCL | MSETCL | MSETCL | 1 | Twin ACSR Moose | 517.1749 | 0.555 | - | - | - | - | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
238 | Magarawada | Kala | 1 | WRTS-2 | WRTS-2 | WRTS-2 | 53 | Twin ACSR Moose | 517.1749 | 29.415 | - | - | - | - | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
239 | Magarawada | Kala | 2 | WRTS-2 | WRTS-2 | WRTS-2 | 53 | Twin ACSR Moose | 517.1749 | 29.415 | - | - | - | - | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
240 | Magarawada | Navsari | 1 | WRTS-2 | WRTS-2 | WRTS-2 | 126 | Twin ACSR Moose | 517.1749 | 69.93 | - | - | - | - | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
241 | Magarawada | Navsari | 2 | WRTS-2 | WRTS-2 | WRTS-2 | 126 | Twin ACSR Moose | 517.1749 | 69.93 | - | - | - | - | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
242 | Malwa | Chhegaon | 1 | MPPTCL | MPPTCL | MPPTCL | 53 | Twin ACSR Moose | 517.1749 | 29.415 | - | - | - | - | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
243 | Malwa | Pithampur | 1 | MPPTCL | MPPTCL | MPPTCL | 136 | Twin ACSR Moose | 517.1749 | 75.48 | - | - | - | - | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
244 | Malwa | Pithampur | 2 | MPPTCL | MPPTCL | MPPTCL | 136 | Twin ACSR Moose | 517.1749 | 75.48 | - | - | - | - | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
245 | Malwa | Julwania | 1 | MPPTCL | MPPTCL | MPPTCL | 170 | Twin ACSR Moose | 517.1749 | 94.35 | - | - | - | - | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
246 | Mansar | Chorania | 1 | WRTS-2 | GETCO | GETCO | 94 | Triple ACSR Snowbird | 625.887 | 63.262 | - | - | 63 | - | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0
247 | MCCPL | Bilaspur | 1 | WRTS-1 | MCCPL | WRTS-1 | 45 | Twin ACSR Moose | 517.1749 | 24.975 | - | - | - | - | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
248 | Nagda | Dehgam | 1 | WRTS-2 | MPPTCL | WRTS-2 | 331 | Twin ACSR Moose | 517.1749 | 183.705 | 50 | - | 50 | - | [5 empty] | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0
249 | Nagda | Dehgam | 2 | WRTS-2 | MPPTCL | WRTS-2 | 331 | Twin ACSR Moose | 517.1749 | 183.705 | 50 | - | 50 | - | [5 empty] | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0
250 | Nagda | Shujalpur | 1 | WRTS-2 | MPPTCL | WRTS-2 | 202 | Twin ACSR Moose | 517.1749 | 112.11 | - | - | 63 | Yes | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0
251 | Nagda | Shujalpur | 2 | WRTS-2 | MPPTCL | WRTS-2 | 152 | Twin ACSR Moose | 517.1749 | 84.36 | - | - | 63 | Yes | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0
252 | Nandgaonpeth | Koradi | 1 | MSETCL | MSETCL | MSETCL | 140 | Twin ACSR Moose | 517.1749 | 77.7 | - | - | - | - | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
253 | Navsari | DGEN | 1 | TPL | WRTS-2 | DGEN | 105 | Twin ACSR Moose | 517.1749 | 58.275 | - | - | - | - | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
254 | Navsari | DGEN | 2 | TPL | WRTS-2 | DGEN | 105 | Twin ACSR Moose | 517.1749 | 58.275 | - | - | - | - | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
255 | NSPCL | Raipur | 1 | NSPCL | NSPCL | WRTS-1 | 14 | Twin ACSR Moose | 517.1749 | 7.77 | - | - | - | - | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
256 | NSPCL | Raipur | 2 | NSPCL | NSPCL | WRTS-1 | 14 | Twin ACSR Moose | 517.1749 | 7.77 | - | - | - | - | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
257 | Padghe | Boisar | 1 | WRTS-2 | MSETCL | WRTS-2 | 101 | Twin ACSR Moose | 517.1749 | 56.055 | 50 | - | - | - | [5 empty] | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
258 | Padghe | Nagothane | 1 | MSETCL | MSETCL | MSETCL | 116 | Twin ACSR Moose | 517.1749 | 64.38 | - | - | - | - | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
259 | Padghe | Nagothane | 2 | MSETCL | MSETCL | MSETCL | 116 | Twin ACSR Moose | 517.1749 | 64.38 | - | - | - | - | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
260 | Padghe | Pune-PG | 1 | MSETCL | MSETCL | WRTS-1 | 96 | Twin ACSR Moose | 517.1749 | 53.28 | - | - | - | - | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
261 | Parli-M | Lonikhand-II | 1 | MSETCL | MSETCL | MSETCL | 284 | Twin ACSR Moose | 517.1749 | 157.62 | 50 | - | 50 | - | [5 empty] | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0
262 | Parli-M | Lonikhand-II | 2 | MSETCL | MSETCL | MSETCL | 284 | Twin ACSR Moose | 517.1749 | 157.62 | 50 | - | 50 | - | [5 empty] | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0
263 | Parli-M | Sholapur-M | 1 | MSETCL | MSETCL | MSETCL | 182 | Twin ACSR Moose | 517.1749 | 101.01 | 50 | - | - | - | [5 empty] | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
264 | Parli-M | Chandrapur-II | 1 | MSETCL | MSETCL | MSETCL | 357 | Twin ACSR Moose | 517.1749 | 198.135 | 50 | - | - | - | [5 empty] | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
265 | Parli-M | Nanded | 1 | MSETCL | MSETCL | MSETCL | 163 | Twin ACSR Moose | 517.1749 | 90.465 | 50 | - | - | - | [5 empty] | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
266 | Parli-M | Parli-PG | 1 | WRTS-1 | MSETCL | WRTS-1 | 5 | Twin ACSR Moose | 517.1749 | 2.775 | - | - | - | - | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
267 | Parli-M | Parli-PG | 2 | WRTS-1 | MSETCL | WRTS-1 | 5 | Twin ACSR Moose | 517.1749 | 2.775 | - | - | - | - | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
268 | Parli-PG | Pune-PG(Shikrapur) | 1 | WRTMPL/WRTS-1 | WRTS-1 | WRTS-1 | 272 | Twin ACSR Moose | 517.1749 | 150.96 | 50 | - | 50 | - | [5 empty] | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0
269 | Parli-PG | Pune-PG(Shikrapur) | 2 | WRTMPL/WRTS-1 | WRTS-1 | WRTS-1 | 272 | Twin ACSR Moose | 517.1749 | 150.96 | 50 | - | 50 | - | [5 empty] | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0
270 | Parli-PG | Solapur-PG | 1 | WRTMPL/WRTS-1 | WRTS-1 | WRTS-1 | 65 | Twin ACSR Moose | 517.1749 | 36.075 | - | - | - | - | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
271 | Parli-PG | Solapur-PG | 2 | WRTMPL/WRTS-1 | WRTS-1 | WRTS-1 | 65 | Twin ACSR Moose | 517.1749 | 36.075 | - | - | - | - | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
272 | Pathadi | Bilaspur | 1 | LANCO | LANCO | WRTS-1 | 31 | Twin ACSR Moose | 517.1749 | 17.205 | - | - | - | - | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
273 | Pathadi | Bilaspur | 2 | LANCO | LANCO | WRTS-1 | 31 | Twin ACSR Moose | 517.1749 | 17.205 | - | - | - | - | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
274 | Pirana-T | Pirana-PG | 1 | TPL | TPL | WRTS-2 | 6 | Twin ACSR Moose | 517.1749 | 3.33 | - | - | - | - | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
275 | Pirana-T | Pirana-PG | 2 | TPL | TPL | WRTS-2 | 6 | Twin ACSR Moose | 517.1749 | 3.33 | - | - | - | - | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
276 | Pune-PG(Shikrapur) | Pune-PG | 1 | WRTMPL/WRTS-1 | WRTS-1 | WRTS-1 | 64 | Twin ACSR Moose | 517.1749 | 35.52 | - | - | 50 | Yes | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0
277 | Pune-PG(Shikrapur) | Pune-PG | 2 | WRTMPL/WRTS-1 | WRTS-1 | WRTS-1 | 64 | Twin ACSR Moose | 517.1749 | 35.52 | - | - | 50 | Yes | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0
278 | Pune-PG(Shikrapur) | Pune-PG | 3 | WRTS-1 | WRTS-1 | WRTS-1 | 64 | Twin ACSR Moose | 517.1749 | 35.52 | - | - | 50 | Yes | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0
279 | Pune-PG(Shikrapur) | Pune-PG | 4 | WRTS-1 | WRTS-1 | WRTS-1 | 64 | Twin ACSR Moose | 517.1749 | 35.52 | - | - | 50 | Yes | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0
280 | Raigarh | India Bharath | 1 | WRTS-1/ERTS-2 | WRTS-1 | ERTS-2 | 110 | Twin ACSR Moose | 517.1749 | 61.05 | - | - | - | - | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
281 | Raigarh | Jharsuguda | 2 | WRTS-1/ERTS-2 | WRTS-1 | ERTS-2 | 125 | Twin ACSR Moose | 517.1749 | 69.375 | - | - | - | - | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
282 | Raigarh | Rourkela | 1 | WRTS-1/ERTS-2 | WRTS-1 | ERTS-2 | 130 | Twin ACSR Moose | 517.1749 | 72.15 | - | - | - | - | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
283 | Raigarh | Sterlite | 2 | WRTS-1/ERTS-2 | WRTS-1 | ERTS-2 | 130 | Twin ACSR Moose | 517.1749 | 72.15 | - | - | - | - | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
284 | Raigarh | Raipur | 1 | WRTS-1 | WRTS-1 | WRTS-1 | 217 | Twin ACSR Moose | 517.1749 | 120.435 | - | - | 63 | - | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0
285 | Raigarh | Raipur | 2 | WRTS-1 | WRTS-1 | WRTS-1 | 217 | Twin ACSR Moose | 517.1749 | 120.435 | - | - | 63 | - | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0
286 | Raigarh | Raigarh-PS(Kotra) | 1 | WRTS-1 | WRTS-1 | WRTS-1 | 7 | Twin ACSR Moose | 517.1749 | 3.885 | - | - | - | - | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
287 | Raigarh | Raigarh-PS(Kotra) | 2 | WRTS-1 | WRTS-1 | WRTS-1 | 7 | Twin ACSR Moose | 517.1749 | 3.885 | - | - | - | - | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
288 | Raigarh | KSK Mahanadi | 1 | WRTS-1 | WRTS-1 | KSK | 119 | Twin ACSR Moose | 517.1749 | 66.045 | - | - | - | - | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
289 | Raipur | Wardha | 1 | WRTS-1 | WRTS-1 | WRTS-1 | 371 | Quad ACSR Moose | 680.6549 | 271.572 | 63 | - | 63 | - | [5 empty] | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0
290 | Raipur | Wardha | 2 | WRTS-1 | WRTS-1 | WRTS-1 | 371 | Quad ACSR Moose | 680.6549 | 271.572 | 63 | - | 63 | - | [5 empty] | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0
291 | Raipur | Raipur-PS(Durg) | 1 | WRTS-1 | WRTS-1 | WRTS-1 | 22 | Twin ACSR Moose | 517.1749 | 12.21 | - | - | - | - | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
292 | Raipur | Raipur-PS(Durg) | 2 | WRTS-1 | WRTS-1 | WRTS-1 | 22 | Twin ACSR Moose | 517.1749 | 12.21 | - | - | - | - | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
293 | Raipur-PS(Durg) | GMR-CG | 1 | GMR | WRTS-1 | GMR-CG | 65 | Twin ACSR Moose | 517.1749 | 36.075 | - | - | - | - | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
294 | Raipur-PS(Durg) | GMR-CG | 2 | GMR | WRTS-1 | GMR-CG | 65 | Twin ACSR Moose | 517.1749 | 36.075 | - | - | - | - | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
295 | Raita | Marwa | 1 | CSPTCL | CSPTCL | CSPTCL | 141 | Twin ACSR Moose | 517.1749 | 78.255 | - | - | - | - | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
296 | Raita | Marwa | 2 | CSPTCL | CSPTCL | CSPTCL | 141 | Twin ACSR Moose | 517.1749 | 78.255 | - | - | - | - | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
297 | Rajgarh | Nagda | 1 | WRTS-2 | WRTS-2 | MPPTCL | 104 | Twin ACSR Moose | 517.1749 | 57.72 | - | - | 50 | - | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0
298 | Rajgarh | Nagda | 2 | WRTS-2 | WRTS-2 | MPPTCL | 104 | Twin ACSR Moose | 517.1749 | 57.72 | - | - | 50 | - | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0
299 | Rajgarh | Kasor | 1 | WRTGPL | WRTS-2 | GETCO | 243 | Twin ACSR Moose | 517.1749 | 134.865 | - | - | 50 | - | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0
300 | Rajgarh | Kasor | 2 | WRTGPL | WRTS-2 | GETCO | 243 | Twin ACSR Moose | 517.1749 | 134.865 | - | - | 50 | - | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0
301 | Ranchodpura | Zerda(Kansari) | 1 | WRTGPL | GETCO | GETCO | 140 | Twin ACSR Moose | 517.1749 | 77.7 | - | - | - | - | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
302 | Ranchodpura | Zerda(Kansari) | 2 | WRTGPL | GETCO | GETCO | 140 | Twin ACSR Moose | 517.1749 | 77.7 | - | - | - | - | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
303 | Ranchodpura | Chorania | 1 | WRTGPL | GETCO | GETCO | 103 | Twin ACSR Moose | 517.1749 | 57.165 | - | - | - | - | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
304 | Ranchodpura | Chorania | 2 | WRTGPL | GETCO | GETCO | 103 | Twin ACSR Moose | 517.1749 | 57.165 | - | - | - | - | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
305 | RGPPL | New Koyna | 1 | MSETCL | RGPPL | MSETCL | 60 | Twin ACSR Moose | 517.1749 | 33.3 | - | - | - | - | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
306 | RGPPL | New Koyna | 2 | MSETCL | RGPPL | MSETCL | 60 | Twin ACSR Moose | 517.1749 | 33.3 | - | - | - | - | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
307 | RGPPL | Nagothane | 1 | MSETCL | RGPPL | MSETCL | 136 | Twin ACSR Moose | 517.1749 | 75.48 | - | - | - | - | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
308 | RGPPL | Nagothane | 2 | MSETCL | RGPPL | MSETCL | 136 | Twin ACSR Moose | 517.1749 | 75.48 | - | - | - | - | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
309 | RKM | Raigarh | 1 | WRTS-1 | RKMPPL | WRTS-1 | 6 | Twin ACSR Moose | 517.1749 | 3.33 | - | - | - | - | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
310 | Satna | Bina-PG | 1 | WRTS-2 | WRTS-2 | WRTS-2 | 276 | Twin ACSR Moose | 517.1749 | 153.18 | 50 | - | 50 | - | [5 empty] | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0
311 | Satna | Bina-PG | 2 | WRTS-2 | WRTS-2 | WRTS-2 | 276 | Twin ACSR Moose | 517.1749 | 153.18 | 50 | - | 50 | - | [5 empty] | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0
312 | Satna | Bina-NTS | 3 | WRTS-2 | WRTS-2 | NHPTL | 272 | Twin ACSR Moose | 517.1749 | 150.96 | 50 | - | - | - | [5 empty] | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
313 | Satna | Bina-PG | 4 | WRTS-2 | WRTS-2 | WRTS-2 | 273 | Twin ACSR Moose | 517.1749 | 151.515 | 50 | - | 50 | - | [5 empty] | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0
314 | Satna | JP-Nigrie | 1 | Jaypee | WRTS-2 | Jaypee | 161 | Twin ACSR Moose | 517.1749 | 89.355 | - | - | - | - | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
315 | Satna | JP-Nigrie | 2 | Jaypee | WRTS-2 | Jaypee | 161 | Twin ACSR Moose | 517.1749 | 89.355 | - | - | - | - | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
316 | Satpura | Indira sagar | 1 | MPPTCL | MPPTCL | MPPTCL | 189 | Twin ACSR Moose | 517.1749 | 104.895 | - | - | - | - | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
317 | Satpura | Itarsi | 1 | WRTS-2 | MPPTCL | WRTS-2 | 79 | Twin ACSR Moose | 517.1749 | 43.845 | - | - | - | - | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
318 | Satpura | Astha | 1 | MPPTCL | MPPTCL | MPPTCL | 240 | Twin ACSR Moose | 517.1749 | 133.2 | - | - | - | - | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
319 | Satpura | Astha | 2 | MPPTCL | MPPTCL | MPPTCL | 240 | Twin ACSR Moose | 517.1749 | 133.2 | - | - | - | - | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
320 | Seoni | Satpura | 1 | WRTS-1 | WRTS-1 | MPPTCL | 156 | Twin ACSR Moose | 517.1749 | 86.58 | 50 | - | - | - | [5 empty] | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
321 | Seoni | Khandwa | 1 | WRTS-1 | WRTS-1 | WRTS-2 | 352 | Quad AAAC Moose | 643.0276 | 243.936 | 80 | - | 80 | Yes | [5 empty] | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 1 | 0
322 | Seoni | Khandwa | 2 | WRTS-1 | WRTS-1 | WRTS-2 | 352 | Quad AAAC Moose | 643.0276 | 243.936 | 80 | - | 80 | Yes | [5 empty] | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 1 | 0
323 | Sholapur-M | Solapur-PG | 1 | MSETCL | MSETCL | WRTS-1 | 178 | Twin ACSR Moose | 517.1749 | 98.79 | - | - | - | - | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
324 | Shujalpur | RAPP | 1 | RTCL | WRTS-2 | NPCIL | 201 | Twin ACSR Moose | 517.1749 | 111.555 | 50 | - | - | - | [5 empty] | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
325 | Shujalpur | RAPP | 2 | RTCL | WRTS-2 | NPCIL | 201 | Twin ACSR Moose | 517.1749 | 111.555 | 50 | - | - | - | [5 empty] | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
326 | Sipat | Raipur | 1 | WRTS-1 | NTPC | WRTS-1 | 149 | Twin ACSR Moose | 517.1749 | 82.695 | - | - | - | - | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
327 | Sipat | Raipur | 2 | WRTS-1 | NTPC | WRTS-1 | 149 | Twin ACSR Moose | 517.1749 | 82.695 | - | - | - | - | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
328 | Sipat | Raipur | 3 | WRTS-1 | NTPC | WRTS-1 | 149 | Twin ACSR Moose | 517.1749 | 82.695 | - | - | - | - | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
329 | Sipat | Ranchi | 1 | WRTS-1/ERTS-1 | NTPC | ERTS-1 | 405 | Twin ACSR Moose | 517.1749 | 224.775 | 80 | - | - | - | [5 empty] | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0
330 | Sipat | Ranchi | 2 | WRTS-1/ERTS-1 | NTPC | ERTS-1 | 405 | Twin ACSR Moose | 517.1749 | 224.775 | 80 | - | - | - | [5 empty] | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0
331 | SKS | Raigarh-PS(Kotra) | 1 | WRTS-1 | SKS | WRTS-1 | 28 | Twin ACSR Moose | 517.1749 | 15.54 | - | - | - | - | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
332 | SKS | Raigarh-PS(Kotra) | 2 | WRTS-1 | SKS | WRTS-1 | 28 | Twin ACSR Moose | 517.1749 | 15.54 | - | - | - | - | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
333 | Soja | Wanakbori | 1 | GETCO | GETCO | GETCO | 95 | Twin ACSR Moose | 517.1749 | 52.725 | - | - | - | - | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
334 | Soja | Dehgam | 1 | WRTS-2 | GETCO | WRTS-2 | 41 | Twin ACSR Moose | 517.1749 | 22.755 | - | - | - | - | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
335 | Soja | Zerda(Kansari) | 1 | GETCO | GETCO | GETCO | 135 | Twin ACSR Moose | 517.1749 | 74.925 | - | - | - | - | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
336 | Solapur-PG | Solapur-NTPC | 1 | WRTS-1 | NTPC | WRTS-1 | 11 | Twin ACSR Moose | 517.1749 | 6.105 | - | - | - | - | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
337 | Solapur-PG | Solapur-NTPC | 2 | WRTS-1 | NTPC | WRTS-1 | 11 | Twin ACSR Moose | 517.1749 | 6.105 | - | - | - | - | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
338 | SSP | Dhule-MS | 1 | MSETCL | SSNNL | MSETCL | 236 | Twin ACSR Moose | 517.1749 | 130.98 | - | - | 50 | Yes | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0
339 | SSP | Dhule-MS | 2 | MSETCL | SSNNL | MSETCL | 236 | Twin ACSR Moose | 517.1749 | 130.98 | - | - | 50 | Yes | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0
340 | SSP | Asoj | 1 | GETCO | SSNNL | GETCO | 83 | Twin ACSR Moose | 517.1749 | 46.065 | - | - | - | - | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
341 | SSP | Rajgarh | 1 | MPPTCL | SSNNL | MPPTCL | 178 | Twin ACSR Moose | 517.1749 | 98.79 | - | - | - | - | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
342 | SSP | Rajgarh | 2 | MPPTCL | SSNNL | MPPTCL | 178 | Twin ACSR Moose | 517.1749 | 98.79 | - | - | - | - | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
343 | SSP | Kasor | 1 | GETCO | SSNNL | GETCO | 146 | Twin ACSR Moose | 517.1749 | 81.03 | - | - | - | - | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
344 | Sugen | Uno-Sugen | 1 | TPL | TPL | TPL | 3 | Twin ACSR Moose | 517.1749 | 1.665 | - | - | - | - | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
345 | Sugen | Pirana-T | 1 | TPL | TPL | TPL | 212 | Twin ACSR Moose | 517.1749 | 117.66 | - | - | 50 | - | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0
346 | Taptithanda | Deepnagar | 1 | MSETCL | MSETCL | MSETCL | 203 | Twin ACSR Moose | 517.1749 | 112.665 | - | - | - | - | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
347 | Taptithanda | Ektuni (Aurangabad(3)) | 1 | MSETCL | MSETCL | MSETCL | 5.36 | Twin ACSR Moose | 517.1749 | 2.9748 | - | - | - | - | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
348 | Tarapur-3&4 | Padghe | 1 | WRTS-1 | NPCIL | MSETCL | 91 | Twin ACSR Moose | 517.1749 | 50.505 | - | - | - | - | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
349 | Tarapur-3&4 | Padghe | 2 | WRTS-1 | NPCIL | MSETCL | 91 | Twin ACSR Moose | 517.1749 | 50.505 | - | - | - | - | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
350 | Tarapur-3&4 | Boisar | 1 | WRTS-2 | NPCIL | WRTS-2 | 21 | Twin ACSR Moose | 517.1749 | 11.655 | - | - | - | - | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
351 | Tarapur-3&4 | Boisar | 2 | WRTS-2 | NPCIL | WRTS-2 | 21 | Twin ACSR Moose | 517.1749 | 11.655 | - | - | - | - | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
352 | Tiroda | Warora | 1 | MEGPTL | APML | MEGPTL | 219 | Twin ACSR Moose | 517.1749 | 121.545 | - | - | - | - | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
353 | Tiroda | Warora | 2 | MEGPTL | APML | MEGPTL | 219 | Twin ACSR Moose | 517.1749 | 121.545 | - | - | - | - | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
354 | TRN | Tamnar-PS | 1 | WRTS-1 | TRN | WRTS-1 | 15 | Twin ACSR Moose | 517.1749 | 8.325 | - | - | - | - | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
355 | TRN | Tamnar-PS | 2 | WRTS-1 | TRN | WRTS-1 | 15 | Twin ACSR Moose | 517.1749 | 8.325 | - | - | - | - | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
356 | Ukai | Kosamba | 1 | GETCO | GETCO | GETCO | 81 | Twin ACSR Moose | 517.1749 | 44.955 | - | - | - | - | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
357 | Ukai | Kosamba | 2 | GETCO | GETCO | GETCO | 68 | Twin ACSR Moose | 517.1749 | 37.74 | - | - | - | - | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
358 | Ukai | Navsari | 1 | GETCO | GETCO | WRTS-2 | 83 | Twin ACSR Moose | 517.1749 | 46.065 | - | - | - | - | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
359 | Uno-Sugen | Pirana-T | 1 | TPL | TPL | TPL | 209 | Twin ACSR Moose | 517.1749 | 115.995 | - | - | 50 | - | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0
360 | Vadinar | Bachau | 1 | WRTS-2 | ESSAR | WRTS-2 | 226 | Twin ACSR Moose | 517.1749 | 125.43 | - | - | 63 | - | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0
361 | Vadinar | Bachau | 2 | WRTS-2 | ESSAR | WRTS-2 | 226 | Twin ACSR Moose | 517.1749 | 125.43 | - | - | 63 | - | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0
362 | Vadodara-PS | Pirana-PG | 1 | WRTS-2 | WRTS-2 | WRTS-2 | 131 | Quad ACSR Moose | 680.6549 | 95.892 | - | - | - | - | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
363 | Vadodara-PS | Pirana-PG | 2 | WRTS-2 | WRTS-2 | WRTS-2 | 131 | Quad ACSR Moose | 680.6549 | 95.892 | - | - | - | - | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
364 | Vadodara-PS | Asoj | 1 | WRTS-2 | WRTS-2 | GETCO | 14 | Quad ACSR Moose | 680.6549 | 10.248 | - | - | - | - | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
365 | Vadodara-PS | Asoj | 2 | WRTS-2 | WRTS-2 | GETCO | 14 | Quad ACSR Moose | 680.6549 | 10.248 | - | - | - | - | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
366 | Vapi | Boisar | 1 | WRTS-2 | WRTS-2 | WRTS-2 | 91 | Twin ACSR Moose | 517.1749 | 50.505 | - | - | - | - | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
367 | Vapi | Sugen | 1 | WRTS-2 | WRTS-2 | TPL | 118 | Twin ACSR Moose | 517.1749 | 65.49 | - | - | - | - | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
368 | Vindhyachal | Jabalpur | 1 | WRTS-2 | NTPC | WRTS-2 | 360 | Twin ACSR Moose | 517.1749 | 199.8 | 63 | - | 63 | - | [5 empty] | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0
369 | Vindhyachal | Jabalpur | 2 | WRTS-2 | NTPC | WRTS-2 | 360 | Twin ACSR Moose | 517.1749 | 199.8 | 63 | - | 63 | - | [5 empty] | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0
370 | Vindhyachal | Jabalpur | 4 | WRTS-2 | NTPC | WRTS-2 | 389 | Twin ACSR Moose | 517.1749 | 215.895 | 63 | - | 63 | - | [5 empty] | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0
371 | Vindhyachal | Satna | 1 | WRTS-2 | NTPC | WRTS-2 | 267 | Twin ACSR Moose | 517.1749 | 148.185 | 50 | - | 50 | - | [5 empty] | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0
372 | Vindhyachal | Satna | 2 | WRTS-2 | NTPC | WRTS-2 | 267 | Twin ACSR Moose | 517.1749 | 148.185 | 50 | - | 50 | - | [5 empty] | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0
373 | Vindhyachal | Satna | 3 | WRTS-2 | NTPC | WRTS-2 | 258 | Twin ACSR Moose | 517.1749 | 143.19 | 50 | - | 50 | - | [5 empty] | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0
374 | Vindhyachal | Satna | 4 | WRTS-2 | NTPC | WRTS-2 | 258 | Twin ACSR Moose | 517.1749 | 143.19 | 50 | - | 50 | - | [5 empty] | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0
375 | Vindhyachal | Sasan | 3 | WRTS-2 | NTPC | SPL | 20 | Twin ACSR Moose | 517.1749 | 11.1 | 63 | Yes | - | - | [5 empty] | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
376 | Vindhyachal | Essar_Mahan | 1 | WRTS-2 | NTPC | Mahan | 41 | Twin ACSR Moose | 517.1749 | 22.755 | 50 | - | - | - | [5 empty] | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
377 | Vindhyachal-III | Vindhyachal-V | 1 | NTPC | NTPC | NTPC | 4 | Quad ACSR Moose | 680.6549 | 2.928 | - | - | - | - | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
378 | Vindhyachal-III | Vindhyachal-V | 2 | NTPC | NTPC | NTPC | 4 | Quad ACSR Moose | 680.6549 | 2.928 | - | - | - | - | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
379 | Vindhyachal-IV | Vindhyachal-V | 1 | NTPC | NTPC | NTPC | 4 | Quad ACSR Moose | 680.6549 | 2.928 | - | - | - | - | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
380 | Vindhyachal-IV | Vindhyachal-V | 2 | NTPC | NTPC | NTPC | 4 | Quad ACSR Moose | 680.6549 | 2.928 | - | - | - | - | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
381 | Vindhyachal-IV | Vindhyachal-PS | 1 | WRTS-2 | NTPC | WRTS-2 | 31 | Twin ACSR Moose | 517.1749 | 17.205 | - | - | - | - | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
382 | Vindhyachal-IV | Vindhyachal-PS | 2 | WRTS-2 | NTPC | WRTS-2 | 31 | Twin ACSR Moose | 517.1749 | 17.205 | - | - | - | - | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
383 | Vindhyachal-PS | Sasan | 1 | WRTS-2 | NTPC | SPL | 8 | Twin ACSR Moose | 517.1749 | 4.44 | - | - | - | - | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
384 | Vindhyachal-PS | Sasan | 2 | WRTS-2 | WRTS-2 | SPL | 8 | Twin ACSR Moose | 517.1749 | 4.44 | - | - | - | - | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
385 | Vindhyachal-PS | Rihand | 1 | WRTS-2/NRTS-1 | WRTS-2 | NRTS-1 | 35 | Quad Bersimis | 691.5238 | 26.11 | - | - | - | - | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
386 | Vindhyachal-PS | Rihand | 2 | WRTS-2/NRTS-1 | WRTS-2 | NRTS-1 | 28 | Quad Bersimis | 691.5238 | 20.888 | - | - | - | - | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
387 | Wardha | Parli-PG | 1 | WRTS-1 | WRTS-1 | WRTS-1 | 337 | Quad ACSR Moose | 680.6549 | 246.684 | 63 | - | 63 | - | [5 empty] | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0
388 | Wardha | Parli-PG | 2 | WRTS-1 | WRTS-1 | WRTS-1 | 337 | Quad ACSR Moose | 680.6549 | 246.684 | 63 | - | 63 | - | [5 empty] | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0
389 | Wardha | Akola | 1 | WRTS-1 | WRTS-1 | MSETCL | 162 | Twin ACSR Moose | 517.1749 | 89.91 | - | - | - | - | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
390 | Wardha | Akola | 2 | WRTS-1 | WRTS-1 | MSETCL | 162 | Twin ACSR Moose | 517.1749 | 89.91 | - | - | - | - | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
391 | Wardha | Mouda | 1 | WRTS-1 | WRTS-1 | NTPC | 124 | Quad ACSR Moose | 680.6549 | 90.768 | - | - | - | - | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
392 | Wardha | Mouda | 2 | WRTS-1 | WRTS-1 | NTPC | 124 | Quad ACSR Moose | 680.6549 | 90.768 | - | - | - | - | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
393 | Wardha | Warora | 1 | WRTS-1 | WRTS-1 | MEGPTL | 76 | Twin ACSR Moose | 517.1749 | 42.18 | - | - | - | - | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
394 | Wardha | Koradi-II | 1 | WRTS-1 | WRTS-1 | IEPL | 67 | Quad ACSR Moose | 680.6549 | 49.044 | - | - | - | - | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
395 | Warora | Chandrapur-II | 1 | MEGPTL | MEGPTL | MSETCL | 45 | Twin ACSR Moose | 517.1749 | 24.975 | - | - | - | - | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
396 | Warora | Chandrapur-II | 2 | MEGPTL | MEGPTL | MSETCL | 45 | Twin ACSR Moose | 517.1749 | 24.975 | - | - | - | - | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
397 | Zerda(Kansari) | Bhinmal | 1 | WRTS-2/NRTS-1 | GETCO | NRTS-1 | 143 | Twin ACSR Moose | 517.1749 | 79.365 | 50 | - | 50 | - | [5 empty] | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0
398 | Zerda(Kansari) | Kankroli | 1 | WRTS-2/NRTS-1 | GETCO | NRTS-1 | 234 | Twin ACSR Moose | 517.1749 | 129.87 | 50 | - | - | - | [5 empty] | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
399 | Zerda(Kansari) | Varsana | 1 | GETCO | GETCO | GETCO | 258 | Twin ACSR Moose | 517.1749 | 143.19 | 63 | - | - | - | [5 empty] | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[6 empty] | Total | 52887.16 |  |  |  | 5233 | Total | 5648 | [6 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[10 empty] | 30087.8118 |  |  | 2 | [6 empty] | 3 | 64 | 7 | 14 | 2 | 5 | 9 | 60 | 2 | 24 | 3 | 4
[20 empty] | 150 | 3200 | 441 | 882 | 160 | 400 | 450 | 3000 | 126 | 1512 | 240 | 320
[22 empty] | 5233 | [5 empty] | 5648
10881

## 400 kV SS Res
Sr. No. | Name of S/S | S/S Owner | Lines | ID | Line Length (in km) | Conductor Type | LRs | LRs S/W | BRs | Line Owner | End-2 Owner | 50 MVAR SLRs | 50 MVAR NSLRs | 63 MVAR SLRs | 63 MVAR NSLRs | 80 MVAR SLRs | 80 MVAR NSLRs
1 | ACBIL | ACBIL | Bilaspur | 1 | 56 | Twin ACSR Moose | - | - | - |  |  | 0 | 0 | 0 | 0 | 0 | 0
|  |  | MCCPL | 1 | 16 | Twin ACSR Moose | - | - |  |  |  | 0 | 0 | 0 | 0 | 0 | 0
|  | Total |  |  |  |  | - |  | - |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 5
2 | Akola | MSETCL | Aurangabad-PG | 1 | 178 | Twin ACSR Moose | 50 | - | - |  |  | 0 | 1 | 0 | 0 | 0 | 0 | 5
|  |  | Aurangabad-PG | 2 | 178 | Twin ACSR Moose | 50 | - |  |  |  | 0 | 1 | 0 | 0 | 0 | 0 | 5
|  |  | Nandgaonpeth | 1 | 117 | Twin ACSR Moose | - | - |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 5
|  |  | Akola(2) | 1 | 30 | Twin ACSR Moose | - | - |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 5
|  |  | Akola(2) | 2 | 30 | Twin ACSR Moose | - | - |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 5
|  |  | Bhusawal (Khadka) | 1 | 182 | Twin ACSR Moose | - | - |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 5
|  |  | Wardha | 1 | 162 | Twin ACSR Moose | - | - |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 5
|  |  | Wardha | 2 | 162 | Twin ACSR Moose | - | - |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 5
|  | Total |  |  |  |  | 100 |  |  |  |  | 0 | 2 | 0 | 0 | 0 | 0 | 12 | 14
3 | Akola(2) | MSETCL | Nandgaonpeth | 1 | 104 | Twin ACSR Moose | - | - | - |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 12 | 14
|  |  | Nandgaonpeth | 2 | 104 | Twin ACSR Moose | - | - |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 12 | 14
|  |  | Akola | 1 | 30 | Twin ACSR Moose | - | - |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 12 | 14
|  |  | Akola | 2 | 30 | Twin ACSR Moose | - | - |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 12 | 14
|  | Total |  |  |  |  | - |  |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 17 | 19
4 | Amreli | GETCO | Hadala | 1 | 165 | Twin ACSR Moose | - | - | 1X50 + 1X125 |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 17 | 19
|  |  | Chorania | 1 | 164 | Twin ACSR Moose | - | - |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 17 | 19
|  |  | Jetpur | 1 | 96 | Twin ACSR Moose | - | - |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 17 | 19
|  |  | Jetpur | 2 | 96 | Twin ACSR Moose | - | - |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 17 | 19
|  | Total |  |  |  |  | - | - | 175 |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 22 | 24
5 | APL-Mundra | APL | Sami | 1 | 282 | Twin ACSR Moose | - | - | 2X80 + 1X125 |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 22 | 24
|  |  | Sami | 2 | 282 | Twin ACSR Moose | - | - |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 22 | 24
|  |  | Hadala | 1 | 233 | Twin ACSR Moose | - | - |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 22 | 24
|  |  | Varsana | 1 | 84 | Twin ACSR Moose | - | - |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 22 | 24
|  |  | Varsana | 2 | 84 | Twin ACSR Moose | - | - |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 22 | 24
|  |  | Zerda(Kansari) | 1 | 332 | Twin ACSR Moose | - | - |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 22 | 24
|  | Total |  |  |  |  | - |  | 285 |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 29 | 31
6 | Asoj | GETCO | Chorania | 1 | 177 | Twin ACSR Moose | - | - | 1X50 |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 29 | 31
|  |  | Chorania | 2 | 166 | Twin ACSR Moose | 50 | - |  |  |  | 0 | 1 | 0 | 0 | 0 | 0 | 29 | 31
|  |  | Kosamba | 1 | 122 | Twin ACSR Moose | - | - |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 29 | 31
|  |  | Wanakbori | 1 | 76 | Twin ACSR Moose | - | - |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 29 | 31
|  |  | Indore-MP | 1 | 289 | Twin ACSR Moose | 50 | - |  |  |  | 0 | 1 | 0 | 0 | 0 | 0 | 29 | 31
|  |  | Indore-MP | 2 | 273 | Twin ACSR Moose | 50 | - |  |  |  | 0 | 1 | 0 | 0 | 0 | 0 | 29 | 31
|  |  | SSP | 1 | 83 | Twin ACSR Moose | - | - |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 29 | 31
|  |  | Vadodara-PS | 1 | 14 | Quad ACSR Moose | - | - |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 29 | 31
|  |  | Vadodara-PS | 2 | 14 | Quad ACSR Moose | - | - |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 29 | 31
|  | Total |  |  |  |  | 150 |  | 50 |  |  | 0 | 3 | 0 | 0 | 0 | 0 | 39 | 41
7 | Astha | MPPTCL | Satpura | 1 | 240 | Twin ACSR Moose | - | - | 50 |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 39 | 41
|  |  | Satpura | 2 | 240 | Twin ACSR Moose | - | - |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 39 | 41
|  | Total |  |  |  |  | - |  | 50 |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 42 | 44
8 | Athena | ACPL | Raigarh-PS(Kotra) | 1 | 25 | Quad ACSR Moose | - | - |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 42 | 44
|  |  | Raigarh-PS(Kotra) | 2 | 25 | Quad ACSR Moose | - | - |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 42 | 44
|  | Total |  |  |  |  | - | - | - |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 45 | 47
9 | Aurangabad-M(Waluj) | MSETCL | Pune-PG(Shikrapur) | 1 | 315 | Twin ACSR Moose | 50 | - | - |  |  | 0 | 1 | 0 | 0 | 0 | 0 | 45 | 47
|  |  | Pune-PG(Shikrapur) | 2 | 315 | Twin ACSR Moose | 50 | - |  |  |  | 0 | 1 | 0 | 0 | 0 | 0 | 45 | 47
|  |  | Aurangabad-PG | 1 | 54 | Quad ACSR Moose | - | - |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 45 | 47
|  |  | Aurangabad-PG | 2 | 54 | Quad ACSR Moose | - | - |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 45 | 47
|  |  | Taptithanda | 1 | 135 | Twin ACSR Moose | - | - |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 45 | 47
|  |  | Deepnagar | 2 | 185 | Twin ACSR Moose | - | - |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 45 | 47
|  |  | Bableshwar | 1 | 131 | Twin ACSR Moose | - | - |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 45 | 47
|  |  | Bhusawal (Khadka) | 1 | 238 | Twin ACSR Moose | 50 | - |  |  |  | 0 | 1 | 0 | 0 | 0 | 0 | 45 | 47
|  | Total |  |  |  |  | 150 |  | - |  |  | 0 | 3 | 0 | 0 | 0 | 0 | 54 | 56
10 | Aurangabad-PG | PGCIL | Boisar | 1 | 327 | Twin ACSR Moose | 80 | Yes | 1X125 |  |  | 0 | 0 | 0 | 0 | 1 | 0 | 54 | 56
|  |  | Boisar | 2 | 327 | Twin ACSR Moose | 80 | Yes |  |  |  | 0 | 0 | 0 | 0 | 1 | 0 | 54 | 56
|  |  | Akola | 1 | 178 | Twin ACSR Moose | 50 | - |  |  |  | 0 | 1 | 0 | 0 | 0 | 0 | 54 | 56
|  |  | Akola | 2 | 178 | Twin ACSR Moose | 50 | - |  |  |  | 0 | 1 | 0 | 0 | 0 | 0 | 54 | 56
|  |  | Aurangabad-M(Waluj) | 1 | 54 | Quad ACSR Moose | - | - |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 54 | 56
|  |  | Aurangabad-M(Waluj) | 2 | 54 | Quad ACSR Moose | - | - |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 54 | 56
|  | Total |  |  |  |  | 260 | - | 125 |  |  | 0 | 2 | 0 | 0 | 2 | 0 | 61 | 63
11 | Bableshwar | MSETCL | Padghe | 1 | 174 | Twin ACSR Moose | - | - | 2X80 |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 61 | 63
|  |  | Padghe | 2 | 174 | Twin ACSR Moose | - | - |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 61 | 63
|  |  | Aurangabad-M(Waluj) | 1 | 131 | Twin ACSR Moose | - | - |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 61 | 63
|  |  | IB-Nasik | 1 | 72 | Twin ACSR Moose | - | - |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 61 | 63
|  |  | IB-Nasik | 2 | 72 | Twin ACSR Moose | - | - |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 61 | 63
|  |  | Bhusawal (Khadka) | 1 | 220 | Twin ACSR Moose | - | - |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 61 | 63
|  |  | Dhule | 1 | 170 | Twin ACSR Moose | - | - |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 61 | 63
|  |  | Dhule | 2 | 170 | Twin ACSR Moose | - | - |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 61 | 63
|  |  | Ektuni (Aurangabad(3)) | 1 | 127 | Quad ACSR Moose | - | - |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 61 | 63
|  |  | Ektuni (Aurangabad(3)) | 2 | 127 | Quad ACSR Moose | - | - |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 61 | 63
|  | Total |  |  |  |  | - |  | 160 |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 72 | 74
12 | Bachau | PGCIL | Ranchodpura | 1 | 282 | Triple ACSR Snowbird | - | - | 1X63 + 1X125 |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 72 | 74
|  |  | Ranchodpura | 2 | 282 | Triple ACSR Snowbird | - | - |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 72 | 74
|  |  | Varsana | 1 | 10 | Twin ACSR Moose | - | - |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 72 | 74
|  |  | Varsana | 2 | 10 | Twin ACSR Moose | - | - |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 72 | 74
|  |  | CGPL | 1 | 100 | Triple ACSR Snowbird | - | - |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 72 | 74
|  |  | CGPL | 2 | 100 | Triple ACSR Snowbird | - | - |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 72 | 74
|  |  | Vadinar | 1 | 226 | Twin ACSR Moose | 63 | - |  |  |  | 0 | 0 | 0 | 1 | 0 | 0 | 72 | 74
|  |  | Vadinar | 2 | 226 | Twin ACSR Moose | 63 | - |  |  |  | 0 | 0 | 0 | 1 | 0 | 0 | 72 | 74
|  | Total |  |  |  |  | 126 |  | 188 |  |  | 0 | 0 | 0 | 2 | 0 | 0 | 81 | 83
13 | Balco | Balco | Dharamjaygarh | 1 | 23.2 | Twin ACSR Moose | - | - | - |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 81 | 83
|  |  | Dharamjaygarh | 2 | 23.2 | Twin ACSR Moose | - | - |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 81 | 83
|  | Total |  |  |  |  | - |  |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 84 | 86
14 | Bhadrawati | PGCIL | Bhilai | 1 | 322 | Twin ACSR Moose | 50 | - | 1X50 |  |  | 0 | 1 | 0 | 0 | 0 | 0 | 84 | 86
|  |  | Raipur | 1 | 333 | Twin ACSR Moose | 50 | - |  |  |  | 0 | 1 | 0 | 0 | 0 | 0 | 84 | 86
|  |  | Raipur | 2 | 346 | Twin ACSR Moose | 63 | - |  |  |  | 0 | 0 | 0 | 1 | 0 | 0 | 84 | 86
|  |  | Raipur | 3 | 346 | Twin ACSR Moose | 63 | - |  |  |  | 0 | 0 | 0 | 1 | 0 | 0 | 84 | 86
|  |  | EMCO | 1 | 28 | Twin ACSR Moose | - | - |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 84 | 86
|  |  | EMCO | 2 | 28 | Twin ACSR Moose | - | - |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 84 | 86
|  |  | Parli-PG | 1 | 388 | Twin ACSR Moose | 63 | - |  |  |  | 0 | 0 | 0 | 1 | 0 | 0 | 84 | 86
|  |  | Dhariwal | 1 | 15 | Twin ACSR Moose | 63 | - |  |  |  | 0 | 0 | 0 | 1 | 0 | 0 | 84 | 86
|  |  | Ramagundam | 1 | 178 | Twin ACSR Moose | 50 | - |  |  |  | 0 | 1 | 0 | 0 | 0 | 0 | 84 | 86
|  |  | Ramagundam | 2 | 178 | Twin ACSR Moose | 50 | - |  |  |  | 0 | 1 | 0 | 0 | 0 | 0 | 84 | 86
|  |  | Chandrapur | 1 | 20 | Twin ACSR Moose | - | - |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 84 | 86
|  |  | Chandrapur | 2 | 20 | Twin ACSR Moose | - | - |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 84 | 86
|  |  | Chandrapur | 3 | 22 | Twin ACSR Moose | - | - |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 84 | 86
|  |  | Chandrapur | 4 | 22 | Twin ACSR Moose | - | - |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 84 | 86
|  | Total |  |  |  |  | 452 |  | 50 |  |  | 0 | 4 | 0 | 4 | 0 | 0 | 99 | 101
15 | Bhatapara | PGCIL | Bhilai | 1 | 93 | Twin ACSR Moose | 50 | - | 1X125 |  |  | 0 | 1 | 0 | 0 | 0 | 0 | 99 | 101
|  |  | Korba-NTPC | 1 | 124 | Twin ACSR Moose | - | - |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 99 | 101
|  | Total |  |  |  |  | 50 |  | 125 |  |  | 0 | 1 | 0 | 0 | 0 | 0 | 102 | 104
16 | Bhilai | CSPTCL | Raipur | 1 | 13 | Twin ACSR Moose | - | - | - |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 102 | 104
|  |  | Seoni | 1 | 230 | Twin ACSR Moose | 50 | - | - |  |  | 0 | 1 | 0 | 0 | 0 | 0 | 102 | 104
|  |  | Bhatapara | 1 | 93 | Twin ACSR Moose | - | - |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 102 | 104
|  |  | Raita | 1 | 56 | Twin ACSR Moose | - | - |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 102 | 104
|  |  | Raita | 2 | 56 | Twin ACSR Moose | - | - |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 102 | 104
|  |  | Raita | 3 | 56 | Twin ACSR Moose | - | - |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 102 | 104
|  |  | Bhadrawati | 1 | 322 | Twin ACSR Moose | 80 | - |  |  |  | 0 | 0 | 0 | 0 | 0 | 1 | 102 | 104
|  |  | Koradi | 1 | 272 | Twin ACSR Moose | 50 | - |  |  |  | 0 | 1 | 0 | 0 | 0 | 0 | 102 | 104
|  |  | Korba (W)-Ext | 1 | 220 | Twin ACSR Moose | 50 | - |  |  |  | 0 | 1 | 0 | 0 | 0 | 0 | 102 | 104
|  |  | Korba-NTPC | 1 | 197 | Twin ACSR Moose | 50 | - |  |  |  | 0 | 1 | 0 | 0 | 0 | 0 | 102 | 104
|  |  | Korba-NTPC | 2 | 192 | Twin ACSR Moose | 50 | - |  |  |  | 0 | 1 | 0 | 0 | 0 | 0 | 102 | 104
|  | Total |  |  |  |  | 330 |  |  |  |  | 0 | 5 | 0 | 0 | 0 | 1 | 114 | 116
17 | Bhopal-BDTCL | BDTCL | Bhopal (MP) | 1 | 9 | Twin ACSR Moose | - | - | 1X125 |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 114 | 116
|  |  | Bhopal (MP) | 2 | 9 | Twin ACSR Moose | - | - |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 114 | 116
|  | Total |  |  |  |  | - | - | 125 |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 117 | 119
18 | Bhopal-MP | MPPTCL | Bina-MP | 1 | 289 | Twin ACSR Moose | - | - | 1X125+1x80 |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 117 | 119
|  |  | Bina-MP | 2 | 273 | Twin ACSR Moose | - | - |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 117 | 119
|  |  | Itarsi | 1 | 98 | Twin ACSR Moose | - | - |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 117 | 119
|  |  | Itarsi | 2 | 98 | Twin ACSR Moose | - | - |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 117 | 119
|  |  | Damoh | 1 | 214 | Twin ACSR Moose | 50 | - |  |  |  | 0 | 1 | 0 | 0 | 0 | 0 | 117 | 119
|  |  | Damoh | 2 | 214 | Twin ACSR Moose | 50 | - |  |  |  | 0 | 1 | 0 | 0 | 0 | 0 | 117 | 119
|  |  | Bhopal-BDTCL | 1 | 9 | Twin ACSR Moose | - | - |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 117 | 119
|  |  | Bhopal-BDTCL | 2 | 9 | Twin ACSR Moose | - | - |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 117 | 119
|  | Total |  |  |  |  | 100 |  | 205 |  |  | 0 | 2 | 0 | 0 | 0 | 0 | 126 | 128
19 | Bhusawal (Khadka) | MSETCL | Bableshwar | 1 | 220 | Twin ACSR Moose | - | - | 1X50 |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 126 | 128
|  |  | Aurangabad-M(Waluj) | 1 | 238 | Twin ACSR Moose | - | - |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 126 | 128
|  |  | Akola | 1 | 182 | Twin ACSR Moose | 50 | - |  |  |  | 0 | 1 | 0 | 0 | 0 | 0 | 126 | 128
|  |  | Deepnagar | 1 | 15 | Twin ACSR Moose | - | - |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 126 | 128
|  |  | Deepnagar | 2 | 15 | Twin ACSR Moose | - | - |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 126 | 128
|  |  | Koradi | 2 | 343 | Twin ACSR Moose | 50 | - |  |  |  | 0 | 1 | 0 | 0 | 0 | 0 | 126 | 128
|  | Total |  |  |  |  | 100 |  | 50 |  |  | 0 | 2 | 0 | 0 | 0 | 0 | 133 | 135
20 | Bilaspur | PGCIL | ACBIL | 1 | 56 | Twin ACSR Moose | - | - | - |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 133 | 135
|  |  | MCCPL | 1 | 45 | Twin ACSR Moose | - | - |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 133 | 135
|  |  | Pathadi | 1 | 31 | Twin ACSR Moose | - | - |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 133 | 135
|  |  | Pathadi | 2 | 31 | Twin ACSR Moose | - | - |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 133 | 135
|  | Total |  |  |  |  | - |  |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 138 | 140
21 | Bina-MP | MPPTCL | JP-Bina | 1 | 20 | Twin ACSR Moose | - | - | 1X50 |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 138 | 140
|  |  | Bina-PG | 1 | 3 | Twin ACSR Moose | - | - |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 138 | 140
|  |  | Bina-PG | 2 | 3 | Twin ACSR Moose | - | - |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 138 | 140
|  |  | Bina-PG | 3 | 3 | Twin ACSR Moose | - | - |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 138 | 140
|  |  | Bina-PG | 4 | 3 | Twin ACSR Moose | - | - |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 138 | 140
|  |  | Bhopal | 1 | 289 | Twin ACSR Moose | 50 | - |  |  |  | 0 | 1 | 0 | 0 | 0 | 0 | 138 | 140
|  |  | Bhopal | 2 | 273 | Twin ACSR Moose | 50 | - |  |  |  | 0 | 1 | 0 | 0 | 0 | 0 | 138 | 140
|  | Total |  |  |  |  | 100 |  | 50 |  |  | 0 | 2 | 0 | 0 | 0 | 0 | 146 | 148
22 | Bina-NHPTL |  | Bina-PG | 1 | 0.4 | Twin ACSR Moose | - | - | - | [8 empty] | 146 | 148
|  | Total | [15 empty] | 148 | 150
23 | Bina-NTS | PGCIL | Bina-PG | 1 | 1 | Twin ACSR Moose | - | - | - |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 148 | 150
|  |  | Satna | 3 | 272 | Twin ACSR Moose | - | - |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 148 | 150
|  | Total |  |  |  |  | - | - | - |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 151 | 153
24 | Bina-PG | PGCIL | Shujalpur | 1 | 200 | Twin ACSR Moose | 63 | Yes | 1X125 |  |  | 0 | 0 | 1 | 0 | 0 | 0 | 151 | 153
|  |  | Shujalpur | 2 | 200 | Twin ACSR Moose | 63 | Yes |  |  |  | 0 | 0 | 1 | 0 | 0 | 0 | 151 | 153
|  |  | Bina-MP | 1 | 3 | Twin ACSR Moose | - | - |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 151 | 153
|  |  | Bina-MP | 2 | 3 | Twin ACSR Moose | - | - |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 151 | 153
|  |  | Bina-MP | 3 | 3 | Twin ACSR Moose | - | - |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 151 | 153
|  |  | Bina-MP | 4 | 3 | Twin ACSR Moose | - | - |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 151 | 153
|  |  | Bina-NHPTL | 1 | 0.4 | Twin ACSR Moose | - | - | [9 empty] | 151 | 153
|  |  | Satna | 1 | 276 | Twin ACSR Moose | 50 | - |  |  |  | 0 | 1 | 0 | 0 | 0 | 0 | 151 | 153
|  |  | Satna | 2 | 276 | Twin ACSR Moose | 50 | - |  |  |  | 0 | 1 | 0 | 0 | 0 | 0 | 151 | 153
|  |  | Satna | 3 | 273 | Twin ACSR Moose | 50 | - |  |  |  | 0 | 1 | 0 | 0 | 0 | 0 | 151 | 153
|  |  | Satna | 4 | 273 | Twin ACSR Moose | 50 | - |  |  |  | 0 | 1 | 0 | 0 | 0 | 0 | 151 | 153
|  |  | JP-Bina | 1 | 20 | Twin ACSR Moose | - | - |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 151 | 153
|  | Total |  |  |  |  | 326 |  | 125 |  |  | 0 | 4 | 2 | 0 | 0 | 0 | 164 | 166
25 | Birsingpur | MPPTCL | Katni | 1 | 118 | Twin ACSR Moose | - | - | 1X50 |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 164 | 166
|  |  | Katni | 2 | 118 | Twin ACSR Moose | 63 | - |  |  |  | 0 | 0 | 0 | 1 | 0 | 0 | 164 | 166
|  |  | Balco | 1 | 236 | Twin ACSR Moose | 50 | - |  |  |  | 0 | 1 | 0 | 0 | 0 | 0 | 164 | 166
|  |  | Vandana | 1 | 215 | Twin ACSR Moose | - | - |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 164 | 166
|  |  | Damoh | 1 | 227 | Twin ACSR Moose | - | - |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 164 | 166
|  |  | Damoh | 2 | 227 | Twin ACSR Moose | - | - |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 164 | 166
|  | Total |  |  |  |  | 113 |  | 50 |  |  | 0 | 1 | 0 | 1 | 0 | 0 | 171 | 173
26 | Boisar | PGCIL | Aurangabad-PG | 1 | 327 | Twin ACSR Moose | 80 | - | - |  |  | 0 | 0 | 0 | 0 | 0 | 1 | 171 | 173
|  |  | Aurangabad-PG | 2 | 327 | Twin ACSR Moose | 80 | - |  |  |  | 0 | 0 | 0 | 0 | 0 | 1 | 171 | 173
|  |  | Padghe | 1 | 101 | Twin ACSR Moose | - | - |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 171 | 173
|  |  | Tarapur-3&4 | 1 | 21 | Twin ACSR Moose | - | - |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 171 | 173
|  |  | Tarapur-3&4 | 2 | 21 | Twin ACSR Moose | - | - |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 171 | 173
|  |  | Vapi | 1 | 91 | Twin ACSR Moose | - | - |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 171 | 173
|  | Total |  |  |  |  | 160 |  | - |  |  | 0 | 0 | 0 | 0 | 0 | 2 | 178 | 180
27 | CGPL | CGPL | Chorania | 1 | 314 | Triple ACSR Snowbird | 63 | Yes | 1x63 |  |  | 0 | 0 | 1 | 0 | 0 | 0 | 178 | 180
|  |  | Mansar | 1 | 224 | Triple ACSR Snowbird | 63 | Yes |  |  |  | 0 | 0 | 1 | 0 | 0 | 0 | 178 | 180
|  |  | Jetpur | 1 | 334 | Triple ACSR Snowbird | 63 | Yes |  |  |  | 0 | 0 | 1 | 0 | 0 | 0 | 178 | 180
|  |  | Jetpur | 2 | 334 | Triple ACSR Snowbird | 63 | Yes |  |  |  | 0 | 0 | 1 | 0 | 0 | 0 | 178 | 180
|  |  | Bachau | 1 | 100 | Triple ACSR Snowbird | - | - |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 178 | 180
|  |  | Bachau | 2 | 100 | Triple ACSR Snowbird | - | - |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 178 | 180
|  | Total |  |  |  |  | 252 |  | 63 |  |  | 0 | 0 | 4 | 0 | 0 | 0 | 185 | 187
28 | Chakan | MSETCL | Pune-PG | 1 | 18 | Twin ACSR Moose | - | - | - |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 185 | 187
|  |  | Lonikhand | 1 | 37 | Twin ACSR Moose | - | - |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 185 | 187
|  | Total |  |  |  |  | - |  | - |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 188 | 190
29 | Champa | PGCIL | - | - | - | - | - | - | 1x80 |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 188 | 190
|  | Total |  |  |  |  | - |  | 80 |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 190 | 192
30 | Chandrapur | MSETCL | Bhadrawati | 1 | 20 | Twin ACSR Moose | - | - | - |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 190 | 192
|  |  | Bhadrawati | 2 | 20 | Twin ACSR Moose | - | - |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 190 | 192
|  |  | Bhadrawati | 3 | 22 | Twin ACSR Moose | - | - |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 190 | 192
|  |  | Bhadrawati | 4 | 22 | Twin ACSR Moose | - | - |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 190 | 192
|  |  | Khaparkheda | 1 | 156 | Twin ACSR Moose | - | - |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 190 | 192
|  |  | Parli-M | 3 | 371 | Twin ACSR Moose | 50 | - |  |  |  | 0 | 1 | 0 | 0 | 0 | 0 | 190 | 192
|  |  | Chandrapur-II | 1 | 1 | Twin ACSR Moose | 50 | - |  |  |  | 0 | 1 | 0 | 0 | 0 | 0 | 190 | 192
|  |  | Chandrapur-II | 2 | 1 | Twin ACSR Moose | 50 | - |  |  |  | 0 | 1 | 0 | 0 | 0 | 0 | 190 | 192
|  | Total |  |  |  |  | 150 |  | - |  |  | 0 | 3 | 0 | 0 | 0 | 0 | 199 | 201
31 | Chandrapur-II | MSETCL | Dhariwal | 1 | 8 | Twin ACSR Moose | - | - | - |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 199 | 201
|  |  | Dhariwal | 2 | 8 | Twin ACSR Moose | - | - |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 199 | 201
|  |  | Nanded | 1 | 257 | Twin ACSR Moose | - | - |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 199 | 201
|  |  | Chandrapur | 1 | 1 | Twin ACSR Moose | - | - |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 199 | 201
|  |  | Chandrapur | 2 | 1 | Twin ACSR Moose | - | - |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 199 | 201
|  |  | Parli-M | 1 | 357 | Twin ACSR Moose | - | - |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 199 | 201
|  |  | Warora | 1 | 45 | Twin ACSR Moose | - | - |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 199 | 201
|  |  | Warora | 2 | 45 | Twin ACSR Moose | - | - |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 199 | 201
|  | Total |  |  |  |  | - |  | - |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 208 | 210
32 | Chhegaon | MPPTCL | Julwania | 1 | 114 | Twin ACSR Moose | - | - | 1x50 |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 208 | 210
|  |  | Malwa | 1 | 53 | Twin ACSR Moose | - | - |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 208 | 210
|  | Total |  |  |  |  | - |  | 50 |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 211 | 213
33 | Chorania | GETCO | Kosamba | 1 | 230 | Twin ACSR Moose | 50 | - | 1X50 + 1X125 | GETCO | GETCO | 0 | 1 | 0 | 0 | 0 | 0 | 211 | 213
|  |  | Kosamba | 2 | 230 | Twin ACSR Moose | 50 | - |  | GETCO | GETCO | 0 | 1 | 0 | 0 | 0 | 0 | 211 | 213
|  |  | Amreli | 1 | 164 | Twin ACSR Moose | - | - |  | GETCO | GETCO | 0 | 0 | 0 | 0 | 0 | 0 | 211 | 213
|  |  | Asoj | 1 | 177 | Twin ACSR Moose | - | - |  | GETCO | GETCO | 0 | 0 | 0 | 0 | 0 | 0 | 211 | 213
|  |  | Asoj | 2 | 166 | Twin ACSR Moose | - | - |  | GETCO | GETCO | 0 | 0 | 0 | 0 | 0 | 0 | 211 | 213
|  |  | CGPL | 1 | 314 | Triple ACSR Snowbird | 63 | - |  | WRTS-2 | CGPL | 0 | 0 | 0 | 1 | 0 | 0 | 211 | 213
|  |  | Hadala | 1 | 166 | Twin ACSR Moose | - | - |  | GETCO | GETCO | 0 | 0 | 0 | 0 | 0 | 0 | 211 | 213
|  |  | Kasor | 1 | 103 | Twin ACSR Moose | - | - |  | GETCO | GETCO | 0 | 0 | 0 | 0 | 0 | 0 | 211 | 213
|  |  | Mansar | 1 | 94 | Triple ACSR Snowbird | 63 | - |  | WRTS-2 | GETCO | 0 | 0 | 0 | 1 | 0 | 0 | 211 | 213
|  |  | Ranchodpura | 1 | 103 | Twin ACSR Moose | - | - |  | WRTGPL | GETCO | 0 | 0 | 0 | 0 | 0 | 0 | 211 | 213
|  |  | Ranchodpura | 2 | 103 | Twin ACSR Moose | - | - |  | WRTGPL | GETCO | 0 | 0 | 0 | 0 | 0 | 0 | 211 | 213
|  | Total |  |  |  |  | 226 |  | 175 |  |  | 0 | 2 | 0 | 2 | 0 | 0 | 223 | 225
34 | Damoh | PGCIL | Birsinghpur | 1 | 227 | Twin ACSR Moose | 50 | - | 1X63 + 1X125 |  |  | 0 | 1 | 0 | 0 | 0 | 0 | 223 | 225
|  |  | Birsinghpur | 2 | 227 | Twin ACSR Moose | 50 | - |  |  |  | 0 | 1 | 0 | 0 | 0 | 0 | 223 | 225
|  |  | Katni | 1 | 118 | Twin ACSR Moose | 50 | - |  |  |  | 0 | 1 | 0 | 0 | 0 | 0 | 223 | 225
|  |  | Bhopal | 1 | 214 | Twin ACSR Moose | - | - |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 223 | 225
|  |  | Bhopal | 2 | 214 | Twin ACSR Moose | - | - |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 223 | 225
|  | Total |  |  |  |  | 150 |  | 188 |  |  | 0 | 3 | 0 | 0 | 0 | 0 | 229 | 231
35 | DB-Power | DB-Power | Raigarh-PS(Kotra) | 1 | 18 | Twin ACSR Moose | - | - | - |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 229 | 231
|  |  | Raigarh-PS(Kotra) | 2 | 18 | Twin ACSR Moose | - | - |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 229 | 231
|  | Total |  |  |  |  | - |  | - |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 232 | 234
36 | Deepnagar | MSETCL | Aurangabad-M(Waluj) | 2 | 185 | Twin ACSR Moose | - | - | - |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 232 | 234
|  |  | Bhusawal (Khadka) | 1 | 15 | Twin ACSR Moose | - | - |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 232 | 234
|  |  | Bhusawal (Khadka) | 2 | 15 | Twin ACSR Moose | - | - |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 232 | 234
|  |  | Taptithanda | 1 | 203 | Twin ACSR Moose | - | - |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 232 | 234
|  | Total |  |  |  |  | - |  | - |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 237 | 239
37 | Dehgam | PGCIL | Gandhar | 1 | 157 | Twin ACSR Moose | - | - | 1X63 + 1X125 |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 237 | 239
|  |  | Gandhar | 2 | 157 | Twin ACSR Moose | - | - |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 237 | 239
|  |  | Pirana-PG | 1 | 56 | Twin ACSR Moose | - | - |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 237 | 239
|  |  | Pirana-PG | 2 | 56 | Twin ACSR Moose | - | - |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 237 | 239
|  |  | Sami | 1 | 152 | Twin ACSR Moose | - | - |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 237 | 239
|  |  | Sami | 2 | 152 | Twin ACSR Moose | - | - |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 237 | 239
|  |  | Ranchodpura | 1 | 62 | Twin ACSR Moose | - | - |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 237 | 239
|  |  | Ranchodpura | 2 | 62 | Twin ACSR Moose | - | - |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 237 | 239
|  |  | Wanakbori | 1 | 68 | Twin ACSR Moose | - | - |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 237 | 239
|  |  | Nagda | 1 | 331 | Twin ACSR Moose | 50 | - |  |  |  | 0 | 1 | 0 | 0 | 0 | 0 | 237 | 239
|  |  | Nagda | 2 | 331 | Twin ACSR Moose | 50 | - |  |  |  | 0 | 1 | 0 | 0 | 0 | 0 | 237 | 239
|  |  | Soja | 1 | 41 | Twin ACSR Moose | - | - |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 237 | 239
|  | Total |  |  |  |  | 100 |  | 187 |  |  | 0 | 2 | 0 | 0 | 0 | 0 | 250 | 252
38 | DGEN | DGEN | Navsari | 1 | 105 | Twin ACSR Moose | - | - | 1X125 |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 250 | 252
|  |  | Navsari | 2 | 105 | Twin ACSR Moose | - | - |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 250 | 252
|  | Total |  |  |  |  | - |  | 125 |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 253 | 255
39 | Dhariwal | DIL | Parli-PG | 1 | 390 | Twin ACSR Moose | - | - | 1x80 |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 253 | 255
|  |  | Bhadrawati | 1 | 15 | Twin ACSR Moose | - | - |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 253 | 255
|  | Total |  |  |  |  | - |  | 80 |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 256 | 258
40 | Dhariwal-MS | DIL | Chandrapur-II | 1 | 8 | Twin ACSR Moose | - | - | - |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 256 | 258
|  |  | Chandrapur-II | 2 | 8 | Twin ACSR Moose | - | - |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 256 | 258
|  | Total |  |  |  |  | - |  | - |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 259 | 261
41 | Dhule-BDTCL | BDTCL | Dhule-MS | 1 | 18 | Twin ACSR Moose | - | - | - |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 259 | 261
|  |  | Dhule-MS | 2 | 18 | Twin ACSR Moose | - | - |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 259 | 261
|  | Total |  |  |  |  | - |  | - |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 262 | 264
42 | Dhule-MS | MSETCL | Dhule-BDTCL | 1 | 18 | Twin ACSR Moose | - | - | 1x80 |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 262 | 264
|  |  | Dhule-BDTCL | 2 | 18 | Twin ACSR Moose | - | - |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 262 | 264
|  |  | Bableshwar | 1 | 170 | Twin ACSR Moose | - | - |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 262 | 264
|  |  | Bableshwar | 2 | 170 | Twin ACSR Moose | - | - |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 262 | 264
|  |  | Khandwa | 1 | 262 | Twin ACSR Moose | 50 | - |  |  |  | 0 | 1 | 0 | 0 | 0 | 0 | 262 | 264
|  |  | Khandwa | 2 | 262 | Twin ACSR Moose | 50 | - |  |  |  | 0 | 1 | 0 | 0 | 0 | 0 | 262 | 264
|  |  | SSP | 1 | 236 | Twin ACSR Moose | 50 | Yes |  |  |  | 1 | 0 | 0 | 0 | 0 | 0 | 262 | 264
|  |  | SSP | 2 | 236 | Twin ACSR Moose | 50 | Yes |  |  |  | 1 | 0 | 0 | 0 | 0 | 0 | 262 | 264
|  | Total |  |  |  |  | 200 |  | 80 |  |  | 2 | 2 | 0 | 0 | 0 | 0 | 271 | 273
43 | EMCO | GMR | Bhadrawati | 1 | 28 | Twin ACSR Moose | - | - | 1X80 |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 271 | 273
|  |  | Bhadrawati | 2 | 28 | Twin ACSR Moose | - | - |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 271 | 273
|  | Total |  |  |  |  | - |  | 80 |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 274 | 276
44 | Essar_Mahan | ESSAR | Korba-NTPC | 1 | 218 | Twin ACSR Moose | - | - | 1X80 |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 274 | 276
|  |  | Vindhyachal | 1 | 41 | Twin ACSR Moose | - | - |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 274 | 276
|  | Total |  |  |  |  | - |  | 80 |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 277 | 279
45 | Gandhar | NTPC | Navsari | 1 | 106 | Twin ACSR Moose | - | - | 1X50 |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 277 | 279
|  |  | Kosamba | 1 | 93 | Twin ACSR Moose | - | - |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 277 | 279
|  |  | Hazira | 1 | 97 | Twin ACSR Moose | - | - |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 277 | 279
|  |  | Hazira | 2 | 97 | Twin ACSR Moose | - | - |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 277 | 279
|  |  | GPEC | 1 | 13 | Twin ACSR Moose | - | - |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 277 | 279
|  |  | Sugen | 1 | 64 | Twin ACSR Moose | 50 | - |  |  |  | 0 | 1 | 0 | 0 | 0 | 0 | 277 | 279
|  |  | Dehgam | 1 | 157 | Twin ACSR Moose | - | - |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 277 | 279
|  |  | Dehgam | 2 | 157 | Twin ACSR Moose | - | - |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 277 | 279
|  | Total |  |  |  |  | 50 |  | 50 |  |  | 0 | 1 | 0 | 0 | 0 | 0 | 286 | 288
46 | GMR-CG | GMR | Raipur-PS(Durg) | 1 | 65 | Twin ACSR Moose | - | - | 1x125 |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 286 | 288
|  |  | Raipur-PS(Durg) | 2 | 65 | Twin ACSR Moose | - | - |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 286 | 288
|  | Total | [6 empty] | 125 |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 289 | 291
47 | GPEC | GPEC | Kasor | 1 | 98 | Twin ACSR Moose | - | - | - |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 289 | 291
|  |  | Gandhar | 1 | 13 | Twin ACSR Moose | - | - |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 289 | 291
|  | Total |  |  |  |  | - |  | - |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 292 | 294
48 | Gwalior | PGCIL | - | - | - | - | - | - | 3x125 |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 292 | 294
|  | Total |  |  |  |  | - |  | 375 |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 294 | 296
49 | Hadala | GETCO | Versana | 1 | 159 | Twin ACSR Moose | - | - | 1X50 + 1X125 |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 294 | 296
|  |  | Vadinar | 1 | 113 | Twin ACSR Moose | - | - |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 294 | 296
|  |  | Vadinar | 2 | 113 | Twin ACSR Moose | - | - |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 294 | 296
|  |  | Chorania | 1 | 166 | Twin ACSR Moose | - | - |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 294 | 296
|  |  | Amreli | 1 | 165 | Twin ACSR Moose | - | - |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 294 | 296
|  |  | APL-Mundra | 1 | 233 | Twin ACSR Moose | 63 | - |  |  |  | 0 | 0 | 0 | 1 | 0 | 0 | 294 | 296
|  | Total |  |  |  |  | 63 |  | 175 |  |  | 0 | 0 | 0 | 1 | 0 | 0 | 301 | 303
50 | Hazira | ESSAR | Gandhar | 1 | 97 | Twin ACSR Moose | - | - | - |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 301 | 303
|  |  | Gandhar | 2 | 97 | Twin ACSR Moose | - | - |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 301 | 303
|  | Total |  |  |  |  | - |  | - |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 304 | 306
51 | IEPL | IEPL | Warora | 1 | 150 | Twin ACSR Moose | - | - | - |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 304 | 306
|  |  | Koradi-II | 1 | 94 | Twin ACSR Moose | - | - |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 304 | 306
|  | Total | [6 empty] | - |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 307 | 309
52 | Indira Sagar | MPPTCL | Indore-MP | 1 | 79 | Quad ACSR Moose | - | - | - |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 307 | 309
|  |  | Indore-MP | 2 | 80 | Quad ACSR Moose | - | - |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 307 | 309
|  |  | Nagda | 1 | 188 | Twin ACSR Moose | - | - |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 307 | 309
|  |  | Satpura | 1 | 189 | Twin ACSR Moose | - | - |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 307 | 309
|  | Total |  |  |  |  | - |  | - |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 312 | 314
53 | Indore-MP | MPPTCL | Indore-PG | 1 | 50 | Twin ACSR Moose | - | - | - |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 312 | 314
|  |  | Indore-PG | 2 | 50 | Twin ACSR Moose | - | - |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 312 | 314
|  |  | Nagda | 1 | 108 | Twin ACSR Moose | - | - |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 312 | 314
|  |  | Asoj | 1 | 289 | Twin ACSR Moose | 50 | - |  |  |  | 0 | 1 | 0 | 0 | 0 | 0 | 312 | 314
|  |  | Asoj | 2 | 273 | Twin ACSR Moose | 50 | - |  |  |  | 0 | 1 | 0 | 0 | 0 | 0 | 312 | 314
|  |  | Indira Sagar | 1 | 79 | Quad ACSR Moose | - | - |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 312 | 314
|  |  | Indira Sagar | 2 | 80 | Quad ACSR Moose | 50 | - |  |  |  | 0 | 1 | 0 | 0 | 0 | 0 | 312 | 314
|  |  | Itarsi | 1 | 207 | Twin ACSR Moose | 50 | - |  |  |  | 0 | 1 | 0 | 0 | 0 | 0 | 312 | 314
|  |  | Itarsi | 2 | 214 | Twin ACSR Moose | 50 | - |  |  |  | 0 | 1 | 0 | 0 | 0 | 0 | 312 | 314
|  | Total |  |  |  |  | 250 | - | - |  |  | 0 | 5 | 0 | 0 | 0 | 0 | 322 | 324
54 | Indore-PG | PGCIL | Indore-MP | 1 | 50 | Twin ACSR Moose | - | - | 1X125 + 1X63 |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 322 | 324
|  |  | Indore-MP | 2 | 50 | Twin ACSR Moose | - | - |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 322 | 324
|  |  | Pithampur | 1 | 150 | Twin ACSR Moose | - | - |  | MPPTCL | MPPTCL | 0 | 0 | 0 | 0 | 0 | 0 | 322 | 324
|  |  | Pithampur | 2 | 150 | Twin ACSR Moose | - | - |  | MPPTCL | MPPTCL | 0 | 0 | 0 | 0 | 0 | 0 | 322 | 324
|  | Total | [6 empty] | 188 |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 327 | 329
55 | Itarsi | PGCIL | Indore-MP | 1 | 207 | Twin ACSR Moose | 50 | - | 2X125 + 1X50 |  |  | 0 | 1 | 0 | 0 | 0 | 0 | 327 | 329
|  |  | Indore-MP | 2 | 214 | Twin ACSR Moose | 50 | - |  |  |  | 0 | 1 | 0 | 0 | 0 | 0 | 327 | 329
|  |  | Khandwa | 1 | 197 | Twin ACSR Moose | 50 | Yes |  |  |  | 1 | 0 | 0 | 0 | 0 | 0 | 327 | 329
|  |  | Khandwa | 2 | 197 | Twin ACSR Moose | 50 | - |  |  |  | 0 | 1 | 0 | 0 | 0 | 0 | 327 | 329
|  |  | Bhopal-MP | 1 | 98 | Twin ACSR Moose | - | - |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 327 | 329
|  |  | Bhopal-MP | 2 | 98 | Twin ACSR Moose | - | - |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 327 | 329
|  |  | Jabalpur | 1 | 232 | Twin ACSR Moose | 50 | - |  |  |  | 0 | 1 | 0 | 0 | 0 | 0 | 327 | 329
|  |  | Jabalpur | 2 | 232 | Twin ACSR Moose | 50 | - |  |  |  | 0 | 1 | 0 | 0 | 0 | 0 | 327 | 329
|  |  | Jabalpur | 3 | 234 | Twin ACSR Moose | 50 | - |  |  |  | 0 | 1 | 0 | 0 | 0 | 0 | 327 | 329
|  |  | Jabalpur | 4 | 234 | Twin ACSR Moose | 50 | - |  |  |  | 0 | 1 | 0 | 0 | 0 | 0 | 327 | 329
|  |  | Satpura | 1 | 79 | Twin ACSR Moose | - | - |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 327 | 329
|  | Total |  |  |  |  | 400 |  | 300 |  |  | 1 | 7 | 0 | 0 | 0 | 0 | 339 | 341
56 | Jabalpur | PGCIL | Itarsi | 1 | 232 | Twin ACSR Moose | 50 | - | 1X125 + 1X63 |  |  | 0 | 1 | 0 | 0 | 0 | 0 | 339 | 341
|  |  | Itarsi | 2 | 232 | Twin ACSR Moose | 50 | - |  |  |  | 0 | 1 | 0 | 0 | 0 | 0 | 339 | 341
|  |  | Itarsi | 3 | 234 | Twin ACSR Moose | 50 | Yes |  |  |  | 1 | 0 | 0 | 0 | 0 | 0 | 339 | 341
|  |  | Itarsi | 4 | 234 | Twin ACSR Moose | 50 | Yes |  |  |  | 1 | 0 | 0 | 0 | 0 | 0 | 339 | 341
|  |  | Sasan | 1 | 340 | Twin ACSR Moose | 63 | - |  |  |  | 0 | 0 | 0 | 1 | 0 | 0 | 339 | 341
|  |  | Jabalpur-PS | 1 | 16 | Quad ACSR Moose | - | - |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 339 | 341
|  |  | Jabalpur-PS | 2 | 16 | Quad ACSR Moose | - | - |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 339 | 341
|  |  | Vindhyachal | 1 | 360 | Twin ACSR Moose | 63 | - |  |  |  | 0 | 0 | 0 | 1 | 0 | 0 | 339 | 341
|  |  | Vindhyachal | 2 | 360 | Twin ACSR Moose | 63 | - |  |  |  | 0 | 0 | 0 | 1 | 0 | 0 | 339 | 341
|  |  | Vindhyachal | 4 | 389 | Twin ACSR Moose | 63 | - |  |  |  | 0 | 0 | 0 | 1 | 0 | 0 | 339 | 341
|  | Total |  |  |  |  | 452 |  | 188 |  |  | 2 | 2 | 0 | 4 | 0 | 0 | 350 | 352
57 | Jabalpur (PS) | PGCIL | MB Power | 1 | 246 | Triple ACSR Snowbird | 50 | - | 2X125 |  |  | 0 | 1 | 0 | 0 | 0 | 0 | 350 | 352
|  |  | MB Power | 2 | 246 | Triple ACSR Snowbird | 50 | - |  |  |  | 0 | 1 | 0 | 0 | 0 | 0 | 350 | 352
|  |  | Jhabua Power | 1 | 65 | Twin ACSR Moose | - | - |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 350 | 352
|  |  | Jhabua Power | 2 | 65 | Twin ACSR Moose | - | - |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 350 | 352
|  |  | Jabalpur | 1 | 16 | Quad ACSR Moose | - | - |  | WRTS-2 | WRTS-2 | 0 | 0 | 0 | 0 | 0 | 0 | 350 | 352
|  |  | Jabalpur | 2 | 16 | Quad ACSR Moose | - | - |  | WRTS-2 | WRTS-2 | 0 | 0 | 0 | 0 | 0 | 0 | 350 | 352
|  | Total |  |  |  |  | 100 |  | 250 |  |  | 0 | 2 | 0 | 0 | 0 | 0 | 357 | 359
58 | Jaigad | MSETCL | New koyna | 1 | 55 | Twin ACSR Moose | - | - | 2x50 |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 357 | 359
|  |  | New koyna | 2 | 55 | Twin ACSR Moose | - | - |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 357 | 359
|  |  | Karad | 1 | 111 | Twin ACSR Moose | - | - |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 357 | 359
|  |  | Karad | 2 | 111 | Twin ACSR Moose | - | - |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 357 | 359
|  | Total |  |  |  |  | - |  | 100 |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 362 | 364
59 | Jejuri | MSETCL | Koyna stage-IV | 1 | 172 | Twin ACSR Moose | - | - | - |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 362 | 364
|  |  | Lonikhand | 1 | 48 | Twin ACSR Moose | - | - |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 362 | 364
|  | Total |  |  |  |  | - |  | - |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 365 | 367
60 | Jetpur | GETCO | Amreli | 1 | 96 | Twin ACSR Moose | - | - | 1X50 + 1X63 |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 365 | 367
|  |  | Amreli | 2 | 96 | Twin ACSR Moose | - | - |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 365 | 367
|  |  | CGPL | 1 | 334 | Triple ACSR Snowbird | 63 | - |  |  |  | 0 | 0 | 0 | 1 | 0 | 0 | 365 | 367
|  |  | CGPL | 2 | 334 | Triple ACSR Snowbird | 63 | - |  |  |  | 0 | 0 | 0 | 1 | 0 | 0 | 365 | 367
|  | Total |  |  |  |  | 126 |  | 113 |  |  | 0 | 0 | 0 | 2 | 0 | 0 | 370 | 372
61 | Jhabua Power | Jhabua Power | Jabalpur (PS) | 1 | 65 | Twin ACSR Moose | - | - | - |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 370 | 372
|  |  | Jabalpur (PS) | 2 | 65 | Twin ACSR Moose | - | - |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 370 | 372
|  | Total |  |  |  |  | - |  | - |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 373 | 375
62 | JP-Bina | Jaypee | Bina-MP | 1 | 20 | Twin ACSR Moose | - | - | - |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 373 | 375
|  |  | Bina-PG | 1 | 20 | Twin ACSR Moose | - | - |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 373 | 375
|  | Total |  |  |  |  | - |  | - |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 376 | 378
63 | JPL | JPL | Raipur | 1 | 258 | Twin ACSR Moose | - | - | 1x125 |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 376 | 378
|  |  | Raipur | 2 | 258 | Twin ACSR Moose | - | - |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 376 | 378
|  |  | JPL_extn(Tamnar) | 1 | 2 | Twin ACSR Moose | - | - |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 376 | 378
|  | Total | [6 empty] | 125 |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 380 | 382
64 | JPL_extn(Tamnar) | JPL | Tamnar-PS | 1 | 10 | Twin ACSR Moose | - | - | - |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 380 | 382
|  |  | Tamnar-PS | 2 | 10 | Twin ACSR Moose | - | - |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 380 | 382
|  |  | Tamnar-PS | 3 | 10 | Twin ACSR Moose | - | - |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 380 | 382
|  |  | Tamnar-PS | 4 | 10 | Twin ACSR Moose | - | - |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 380 | 382
|  |  | JPL | 1 | 2 | Twin ACSR Moose | - | - |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 380 | 382
|  | Total |  |  |  |  | - |  | - |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 386 | 388
65 | JP-Nigrie | Jaypee | Satna | 1 | 161 | Twin ACSR Moose | - | - | 1X125 |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 386 | 388
|  |  | Satna | 2 | 161 | Twin ACSR Moose | - | - |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 386 | 388
|  | Total |  |  |  |  | - |  | 125 |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 389 | 391
66 | Julwania | MPPTCL | Chhegaon | 1 | 114 | Twin ACSR Moose | - | - | 1x50 |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 389 | 391
|  |  | Malwa | 1 | 170 | Twin ACSR Moose | - | - |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 389 | 391
|  | Total |  |  |  |  | - |  | 50 |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 392 | 394
67 | Kala | PGCIL | Vapi | 1 | 49 | Twin ACSR Moose | - | - | 1X80 |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 392 | 394
|  |  | Vapi | 2 | 52 | Twin ACSR Moose | - | - |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 392 | 394
|  |  | Magarawada | 1 | 53 | Twin ACSR Moose | - | - |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 392 | 394
|  |  | Magarawada | 2 | 53 | Twin ACSR Moose | - | - |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 392 | 394
|  | Total |  |  |  |  | - |  | 80 |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 397 | 399
68 | Kalwa | MSETCL | Padghe | 1 | 72 | Twin ACSR Moose | - | - | - |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 397 | 399
|  |  | Padghe | 2 | 72 | Twin ACSR Moose | - | - |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 397 | 399
|  |  | Kharghar | 1 | 28 | Twin ACSR Moose | - | - |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 397 | 399
|  |  | Pune-PG | 1 | 104 | Twin ACSR Moose | - | - |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 397 | 399
|  | Total |  |  |  |  | - |  | - |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 402 | 404
69 | Karad | MSETCL | Kolhapur | 1 | 105 | Twin ACSR Moose | - | - | 1X80 | MSETCL | MSETCL | 0 | 0 | 0 | 0 | 0 | 0 | 402 | 404
|  |  | Kolhapur | 2 | 105 | Twin ACSR Moose | - | - |  | MSETCL | MSETCL | 0 | 0 | 0 | 0 | 0 | 0 | 402 | 404
|  |  | Jaigad | 1 | 111 | Twin ACSR Moose | - | - |  | MSETCL | JAIGAD-IPP | 0 | 0 | 0 | 0 | 0 | 0 | 402 | 404
|  |  | Jaigad | 2 | 111 | Twin ACSR Moose | - | - |  | MSETCL | JAIGAD-IPP | 0 | 0 | 0 | 0 | 0 | 0 | 402 | 404
|  |  | New Koyna | 1 | 72 | Twin ACSR Moose | - | - |  | MSETCL | MSETCL | 0 | 0 | 0 | 0 | 0 | 0 | 402 | 404
|  |  | New Koyna | 2 | 72 | Twin ACSR Moose | - | - |  | MSETCL | MSETCL | 0 | 0 | 0 | 0 | 0 | 0 | 402 | 404
|  |  | Solapur-PG | 1 | 299 | Twin ACSR Moose | 50 | - |  | WRTMPL/MSETCL | WRTS-1 | 0 | 1 | 0 | 0 | 0 | 0 | 402 | 404
|  |  | Lonikhand | 1 | 161 | Twin ACSR Moose | 80 | - |  | MSETCL | MSETCL | 0 | 0 | 0 | 0 | 0 | 1 | 402 | 404
|  | Total |  |  |  |  | 130 |  | 80 |  |  | 0 | 1 | 0 | 0 | 0 | 1 | 411 | 413
70 | Kasor | GETCO | Chorania | 1 | 103 | Twin ACSR Moose | - | - | 1X50 + 1X125 | GETCO | GETCO | 0 | 0 | 0 | 0 | 0 | 0 | 411 | 413
|  |  | GPEC | 1 | 98 | Twin ACSR Moose | - | - |  | GPEC | GPEC | 0 | 0 | 0 | 0 | 0 | 0 | 411 | 413
|  |  | Rajgarh | 1 | 243 | Twin ACSR Moose | 50 | - |  | WRTGPL | WRTS-2 | 0 | 1 | 0 | 0 | 0 | 0 | 411 | 413
|  |  | Rajgarh | 2 | 243 | Twin ACSR Moose | 50 | - |  | WRTGPL | WRTS-2 | 0 | 1 | 0 | 0 | 0 | 0 | 411 | 413
|  |  | SSP | 1 | 146 | Twin ACSR Moose | - | - |  | GETCO | SSNNL | 0 | 0 | 0 | 0 | 0 | 0 | 411 | 413
|  | Total |  |  |  |  | 100 |  | 175 |  |  | 0 | 2 | 0 | 0 | 0 | 0 | 417 | 419
71 | Katni | MPPTCL | Birsingpur | 1 | 118 | Twin ACSR Moose | - | - | - | MPPTCL | MPPTCL | 0 | 0 | 0 | 0 | 0 | 0 | 417 | 419
|  |  | Birsingpur | 2 | 118 | Twin ACSR Moose | - | - |  | MPPTCL | MPPTCL | 0 | 0 | 0 | 0 | 0 | 0 | 417 | 419
|  |  | Damoh | 1 | 118 | Twin ACSR Moose | - | - |  | MPPTCL | WRTS-2 | 0 | 0 | 0 | 0 | 0 | 0 | 417 | 419
|  | Total |  |  |  |  | - |  | - |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 421 | 423
72 | Khandwa | PGCIL | Dhule | 1 | 262 | Twin ACSR Moose | 50 | - | 2X125 | WRTS-2 | MSETCL | 0 | 1 | 0 | 0 | 0 | 0 | 421 | 423
|  |  | Dhule | 2 | 262 | Twin ACSR Moose | 50 | - |  | WRTS-2 | MSETCL | 0 | 1 | 0 | 0 | 0 | 0 | 421 | 423
|  |  | Rajgarh | 1 | 221 | Twin ACSR Moose | - | - |  | WRTS-2 | WRTS-2 | 0 | 0 | 0 | 0 | 0 | 0 | 421 | 423
|  |  | Rajgarh | 2 | 221 | Twin ACSR Moose | - | - |  | WRTS-2 | WRTS-2 | 0 | 0 | 0 | 0 | 0 | 0 | 421 | 423
|  |  | Itarsi | 1 | 197 | Twin ACSR Moose | - | - |  | WRTS-2 | WRTS-2 | 0 | 0 | 0 | 0 | 0 | 0 | 421 | 423
|  |  | Itarsi | 2 | 197 | Twin ACSR Moose | - | - |  | WRTS-2 | WRTS-2 | 0 | 0 | 0 | 0 | 0 | 0 | 421 | 423
|  |  | Seoni | 1 | 352 | Quad AAAC Moose | 80 | Yes |  | WRTS-1 | WRTS-1 | 0 | 0 | 0 | 0 | 1 | 0 | 421 | 423
|  |  | Seoni | 2 | 352 | Quad AAAC Moose | 80 | Yes |  | WRTS-1 | WRTS-1 | 0 | 0 | 0 | 0 | 1 | 0 | 421 | 423
|  | Total |  |  |  |  | 260 |  | 250 |  |  | 0 | 2 | 0 | 0 | 2 | 0 | 430 | 432
73 | Khaparkheda | MSETCL | Chandrapur | 1 | 156 | Twin ACSR Moose | - | - | - | MSETCL | MSETCL | 0 | 0 | 0 | 0 | 0 | 0 | 430 | 432
|  |  | Koradi | 1 | 10 | Twin ACSR Moose | - | - |  | MSETCL | MSETCL | 0 | 0 | 0 | 0 | 0 | 0 | 430 | 432
|  |  | Koradi | 2 | 10 | Twin ACSR Moose | - | - |  | MSETCL | MSETCL | 0 | 0 | 0 | 0 | 0 | 0 | 430 | 432
|  | Total |  |  |  |  | - |  | - |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 434 | 436
74 | Kharghar | MSETCL | Padghe | 1 | 85 | Twin ACSR Moose | - | - | 1X80 | MSETCL | MSETCL | 0 | 0 | 0 | 0 | 0 | 0 | 434 | 436
|  |  | Kalwa | 1 | 28 | Twin ACSR Moose | - | - |  | MSETCL | MSETCL | 0 | 0 | 0 | 0 | 0 | 0 | 434 | 436
|  | Total |  |  |  |  | - |  | 80 |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 437 | 439
75 | Kolhapur | MSETCL | Kolhapur-PG | 1 | 39 | Twin ACSR Moose | - | - | 1X80 | WRTS-1 | WRTS-1 | 0 | 0 | 0 | 0 | 0 | 0 | 437 | 439
|  |  | Kolhapur-PG | 2 | 39 | Twin ACSR Moose | - | - |  | WRTS-1 | WRTS-1 | 0 | 0 | 0 | 0 | 0 | 0 | 437 | 439
|  |  | Sholapur-PG | 1 | 220 | Twin ACSR Moose | - | - |  | WRTMPL | WRTS-1 | 0 | 0 | 0 | 0 | 0 | 0 | 437 | 439
|  |  | Sholapur-PG | 2 | 220 | Twin ACSR Moose | - | - |  | WRTMPL | WRTS-1 | 0 | 0 | 0 | 0 | 0 | 0 | 437 | 439
|  |  | Karad | 1 | 105 | Twin ACSR Moose | - | - |  | MSETCL | MSETCL | 0 | 0 | 0 | 0 | 0 | 0 | 437 | 439
|  |  | Karad | 2 | 105 | Twin ACSR Moose | - | - |  | MSETCL | MSETCL | 0 | 0 | 0 | 0 | 0 | 0 | 437 | 439
|  | Total |  |  |  |  | - |  | 80 |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 444 | 446
76 | Kolhapur-PG | PGCIL | Mapusa | 1 | 156 | Twin ACSR Moose | - | - | 1x125 | WRTS-1 | WRTS-1 | 0 | 0 | 0 | 0 | 0 | 0 | 444 | 446
|  |  | Mapusa | 2 | 156 | Twin ACSR Moose | - | - |  | WRTS-1 | WRTS-1 | 0 | 0 | 0 | 0 | 0 | 0 | 444 | 446
|  |  | Kolhapur | 1 | 39 | Twin ACSR Moose | - | - |  | WRTS-1 | MSETCL | 0 | 0 | 0 | 0 | 0 | 0 | 444 | 446
|  |  | Kolhapur | 2 | 39 | Twin ACSR Moose | - | - |  | WRTS-1 | MSETCL | 0 | 0 | 0 | 0 | 0 | 0 | 444 | 446
|  | Total |  |  |  |  | - |  | 125 |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 449 | 451
77 | Koradi | MSETCL | Bhusawal | 2 | 343 | Twin ACSR Moose | 50 | - | 1X50 | MSETCL | MSETCL | 0 | 1 | 0 | 0 | 0 | 0 | 449 | 451
|  |  | Satpura | 1 | 149 | Twin ACSR Moose | - | - |  | WRTS-1 | MPPTCL | 0 | 0 | 0 | 0 | 0 | 0 | 449 | 451
|  |  | Bhilai | 1 | 272 | Twin ACSR Moose | 50 | - |  | WRTS-1 | CSPTCL | 0 | 1 | 0 | 0 | 0 | 0 | 449 | 451
|  |  | Khaparkheda | 1 | 10 | Twin ACSR Moose | - | - |  | MSETCL | MSETCL | 0 | 0 | 0 | 0 | 0 | 0 | 449 | 451
|  |  | Khaparkheda | 2 | 10 | Twin ACSR Moose | - | - |  | MSETCL | MSETCL | 0 | 0 | 0 | 0 | 0 | 0 | 449 | 451
|  |  | Nandgaonpeth | 1 | 140 | Twin ACSR Moose | - | - |  | MSETCL | MSETCL | 0 | 0 | 0 | 0 | 0 | 0 | 449 | 451
|  | Total |  |  |  |  | 100 |  | 50 |  |  | 0 | 2 | 0 | 0 | 0 | 0 | 456 | 458
78 | Koradi-II | MSETCL | IEPL | 2 | 94 | Twin ACSR Moose | - | - | - | WRTS-1 | IEPL | 0 | 0 | 0 | 0 | 0 | 0 | 456 | 458
|  |  | Koradi | 1 | 5 | Twin ACSR Moose | - | - |  | MSETCL | MSETCL | 0 | 0 | 0 | 0 | 0 | 0 | 456 | 458
|  |  | Wardha | 1 | 67 | Quad ACSR Moose | - | - |  | WRTS-1 | WRTS-1 | 0 | 0 | 0 | 0 | 0 | 0 | 456 | 458
|  | Total |  |  |  |  | - |  | - |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 460 | 462
79 | Korba (W) | CSPTCL | Korba-NTPC | 1 | 14 | Twin ACSR Moose | - | - | - | WRTS-1 | NTPC | 0 | 0 | 0 | 0 | 0 | 0 | 460 | 462
|  |  | Raita | 1 | 144 | Twin ACSR Moose | - | - |  | CSPTCL | CSPTCL | 0 | 0 | 0 | 0 | 0 | 0 | 460 | 462
|  |  | Korba (W)-Ext | 1 | 1 | Twin ACSR Moose | - | - |  | CSPTCL | CSPTCL | 0 | 0 | 0 | 0 | 0 | 0 | 460 | 462
|  | Total |  |  |  |  | - |  | - |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 464 | 466
80 | Korba (W)-Ext | CSPTCL | Bhilai | 1 | 220 | Twin ACSR Moose | - | - | - | CSPTCL | CSPTCL | 0 | 0 | 0 | 0 | 0 | 0 | 464 | 466
|  |  | Marwa | 1 | 60 | Twin ACSR Moose | - | - |  | CSPTCL | CSPTCL | 0 | 0 | 0 | 0 | 0 | 0 | 464 | 466
|  |  | Korba (W) | 1 | 1 | Twin ACSR Moose | - | - |  | CSPTCL | CSPTCL | 0 | 0 | 0 | 0 | 0 | 0 | 464 | 466
|  | Total | [6 empty] | - |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 468 | 470
81 | Korba-NTPC | NTPC | Bhilai | 1 | 197 | Twin ACSR Moose | - | - | - | WRTS-1 | CSPTCL | 0 | 0 | 0 | 0 | 0 | 0 | 468 | 470
|  |  | Bhilai | 2 | 192 | Twin ACSR Moose | - | - |  | WRTS-1 | CSPTCL | 0 | 0 | 0 | 0 | 0 | 0 | 468 | 470
|  |  | Raipur | 1 | 212 | Twin ACSR Moose | - | - |  | WRTS-1 | WRTS-1 | 0 | 0 | 0 | 0 | 0 | 0 | 468 | 470
|  |  | Raipur | 2 | 212 | Twin ACSR Moose | - | - |  | WRTS-1 | WRTS-1 | 0 | 0 | 0 | 0 | 0 | 0 | 468 | 470
|  |  | Sipat | 1 | 100 | Twin ACSR Moose | - | - |  | WRTS-1 | NTPC | 0 | 0 | 0 | 0 | 0 | 0 | 468 | 470
|  |  | Essar_Mahan | 1 | 218 | Twin ACSR Moose | - | - |  | WRTS-1 | ESSAR | 0 | 0 | 0 | 0 | 0 | 0 | 468 | 470
|  |  | Vindhyachal | 2 | 289 | Twin ACSR Moose | - | - |  | WRTS-1 | NTPC | 0 | 0 | 0 | 0 | 0 | 0 | 468 | 470
|  |  | Bhatapara | 1 | 124 | Twin ACSR Moose | - | - |  | WRTS-1 | WRTS-1 | 0 | 0 | 0 | 0 | 0 | 0 | 468 | 470
|  |  | Birsingpur | 2 | 260 | Twin ACSR Moose | 50 | - |  | WRTS-2 | BALCO | 0 | 1 | 0 | 0 | 0 | 0 | 468 | 470
|  |  | Vandana | 1 | 18 | Twin ACSR Moose | 50 | - |  | WRTS-2 | Vandana Vidyut | 0 | 1 | 0 | 0 | 0 | 0 | 468 | 470
|  |  | Korba (W) | 1 | 14 | Twin ACSR Moose | - | - |  | WRTS-1 | CSPTCL | 0 | 0 | 0 | 0 | 0 | 0 | 468 | 470
|  | Total |  |  |  |  | 100 |  | - |  |  | 0 | 2 | 0 | 0 | 0 | 0 | 480 | 482
82 | Kosamba | GETCO | Asoj | 1 | 122 | Twin ACSR Moose | - | - | 1X80 | GETCO | GETCO | 0 | 0 | 0 | 0 | 0 | 0 | 480 | 482
|  |  | Chorania | 1 | 230 | Twin ACSR Moose | 63 | - |  | GETCO | GETCO | 0 | 0 | 0 | 1 | 0 | 0 | 480 | 482
|  |  | Chorania | 2 | 230 | Twin ACSR Moose | 63 | - |  | GETCO | GETCO | 0 | 0 | 0 | 1 | 0 | 0 | 480 | 482
|  |  | Gandhar | 1 | 93 | Twin ACSR Moose | - | - |  | GETCO | GETCO | 0 | 0 | 0 | 0 | 0 | 0 | 480 | 482
|  |  | Ukai | 1 | 81 | Twin ACSR Moose | - | - |  | GETCO | GETCO | 0 | 0 | 0 | 0 | 0 | 0 | 480 | 482
|  |  | Ukai | 2 | 68 | Twin ACSR Moose | - | - |  | GETCO | GETCO | 0 | 0 | 0 | 0 | 0 | 0 | 480 | 482
|  | Total |  |  |  |  | 126 |  | 80 |  |  | 0 | 0 | 0 | 2 | 0 | 0 | 487 | 489
83 | Koyna stage-IV | MSETCL | Lonikhand | 1 | 183 | Twin ACSR Moose | - | - | - | MSETCL | MSETCL | 0 | 0 | 0 | 0 | 0 | 0 | 487 | 489
|  |  | New Koyna | 1 | 14 | Twin ACSR Moose | - | - |  | MSETCL | MSETCL | 0 | 0 | 0 | 0 | 0 | 0 | 487 | 489
|  |  | New Koyna | 2 | 14 | Twin ACSR Moose | - | - |  | MSETCL | MSETCL | 0 | 0 | 0 | 0 | 0 | 0 | 487 | 489
|  |  | Jejuri | 1 | 172 | Twin ACSR Moose | - | - |  | MSETCL | MSETCL | 0 | 0 | 0 | 0 | 0 | 0 | 487 | 489
|  | Total |  |  |  |  | - |  | - |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 492 | 494
84 | KSK Mahanadi | KSK | Raipur | 1 | 147 | Twin ACSR Moose | - | - | - | WRTS-1 | WRTS-1 | 0 | 0 | 0 | 0 | 0 | 0 | 492 | 494
|  |  | Raipur | 2 | 150 | Twin ACSR Moose | - | - |  | WRTS-1 | WRTS-1 | 0 | 0 | 0 | 0 | 0 | 0 | 492 | 494
|  |  | RKM | 1 | 104 | Twin ACSR Moose | - | - |  | WRTS-1 | RKMPPL | 0 | 0 | 0 | 0 | 0 | 0 | 492 | 494
|  |  | Raigarh | 1 | 119 | Twin ACSR Moose | - | - |  | WRTS-1 | WRTS-1 | 0 | 0 | 0 | 0 | 0 | 0 | 492 | 494
|  | Total |  |  |  |  | - |  | - |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 497 | 499
85 | KWPCL | KWPCL | Raipur | 1 | 18 | Twin ACSR Moose | - | - | - | WRTS-1 | WRTS-1 | 0 | 0 | 0 | 0 | 0 | 0 | 497 | 499
|  |  | Raigarh | 1 | 217 | Twin ACSR Moose | - | - |  | WRTS-1 | WRTS-1 | 0 | 0 | 0 | 0 | 0 | 0 | 497 | 499
|  | Total |  |  |  |  | - |  | - |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 500 | 502
86 | Lara | NTPC | Raigarh-PS(Kotra) | 1 | 18 | Twin ACSR Moose | - | - | - |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 500 | 502
|  |  | Raigarh-PS(Kotra) | 2 | 18 | Twin ACSR Moose | - | - |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 500 | 502
|  | Total |  |  |  |  | - |  | - |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 503 | 505
87 | Lonikhand | MSETCL | Jejuri | 1 | 48 | Twin ACSR Moose | - | - | 1X50 | MSETCL | MSETCL | 0 | 0 | 0 | 0 | 0 | 0 | 503 | 505
|  |  | Chakan | 1 | 37 | Twin ACSR Moose | 50 | - |  | MSETCL | MSETCL | 0 | 1 | 0 | 0 | 0 | 0 | 503 | 505
|  |  | Pune-PG | 1 | 40 | Twin ACSR Moose | - | - |  | MSETCL | WRTS-1 | 0 | 0 | 0 | 0 | 0 | 0 | 503 | 505
|  |  | Karad | 1 | 161 | Twin ACSR Moose | - | - |  | MSETCL | MSETCL | 0 | 0 | 0 | 0 | 0 | 0 | 503 | 505
|  |  | Koyna stage-IV | 1 | 183 | Twin ACSR Moose | - | - |  | MSETCL | MSETCL | 0 | 0 | 0 | 0 | 0 | 0 | 503 | 505
|  |  | Lonikhand-II | 1 | 1 | Twin ACSR Moose | - | - |  | MSETCL | MSETCL | 0 | 0 | 0 | 0 | 0 | 0 | 503 | 505
|  |  | Lonikhand-II | 2 | 1 | Twin ACSR Moose | - | - |  | MSETCL | MSETCL | 0 | 0 | 0 | 0 | 0 | 0 | 503 | 505
|  | Total |  |  |  |  | 50 |  | 50 |  |  | 0 | 1 | 0 | 0 | 0 | 0 | 511 | 513
88 | Lonikhand-II | MSETCL | Lonikhand | 1 | 1 | Twin ACSR Moose | - | - | - | MSETCL | MSETCL | 0 | 0 | 0 | 0 | 0 | 0 | 511 | 513
|  |  | Lonikhand | 2 | 1 | Twin ACSR Moose | - | - |  | MSETCL | MSETCL | 0 | 0 | 0 | 0 | 0 | 0 | 511 | 513
|  |  | Parli-M | 1 | 284 | Twin ACSR Moose | 50 | - |  | MSETCL | MSETCL | 0 | 1 | 0 | 0 | 0 | 0 | 511 | 513
|  |  | Parli-M | 2 | 284 | Twin ACSR Moose | 50 | - |  | MSETCL | MSETCL | 0 | 1 | 0 | 0 | 0 | 0 | 511 | 513
|  | Total |  |  |  |  | 100 |  | - |  |  | 0 | 2 | 0 | 0 | 0 | 0 | 516 | 518
89 | Magarawada | PGCIL | Kala | 1 | 53 | Twin ACSR Moose | - | - | 1x80 | WRTS-2 | WRTS-2 | 0 | 0 | 0 | 0 | 0 | 0 | 516 | 518
|  |  | Kala | 2 | 53 | Twin ACSR Moose | - | - |  | WRTS-2 | WRTS-2 | 0 | 0 | 0 | 0 | 0 | 0 | 516 | 518
|  |  | Navasari | 1 | 126 | Twin ACSR Moose | - | - |  | WRTS-2 | WRTS-2 | 0 | 0 | 0 | 0 | 0 | 0 | 516 | 518
|  |  | Navasari | 2 | 126 | Twin ACSR Moose | - | - |  | WRTS-2 | WRTS-2 | 0 | 0 | 0 | 0 | 0 | 0 | 516 | 518
|  | Total |  |  |  |  | - |  | 80 |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 521 | 523
90 | Malwa | MPPTCL | Chhegaon | 1 | 53 | Twin ACSR Moose | - | - | - | MPPTCL | MPPTCL | 0 | 0 | 0 | 0 | 0 | 0 | 521 | 523
|  |  | Pithampur | 1 | 136 | Twin ACSR Moose | - | - |  | MPPTCL | MPPTCL | 0 | 0 | 0 | 0 | 0 | 0 | 521 | 523
|  |  | Pithampur | 2 | 136 | Twin ACSR Moose | - | - |  | MPPTCL | MPPTCL | 0 | 0 | 0 | 0 | 0 | 0 | 521 | 523
|  |  | Julwania | 1 | 170 | Twin ACSR Moose | - | - |  | MPPTCL | MPPTCL | 0 | 0 | 0 | 0 | 0 | 0 | 521 | 523
|  | Total |  |  |  |  | - |  | - |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 526 | 528
91 | Mansar | GETCO | Chorania | 1 | 94 | Triple ACSR Snowbird | - | - | 1x63 | WRTS-2 | GETCO | 0 | 0 | 0 | 0 | 0 | 0 | 526 | 528
|  |  | CGPL | 1 | 224 | Triple ACSR Snowbird | - | - |  | WRTS-2 | CGPL | 0 | 0 | 0 | 0 | 0 | 0 | 526 | 528
|  | Total |  |  |  |  | - |  | 63 |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 529 | 531
92 | Mapusa | PGCIL | Kolhapur-PG | 1 | 156 | Twin ACSR Moose | - | - | 1X50 | WRTS-1 | WRTS-1 | 0 | 0 | 0 | 0 | 0 | 0 | 529 | 531
|  |  | Kolhapur-PG | 2 | 156 | Twin ACSR Moose | - | - |  | WRTS-1 | WRTS-1 | 0 | 0 | 0 | 0 | 0 | 0 | 529 | 531
|  | Total |  |  |  |  | - |  | 50 |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 532 | 534
93 | Marwa | CSPTCL | Korba (W)-Ext | 1 | 60 | Twin ACSR Moose | - | - | - | CSPTCL | CSPTCL | 0 | 0 | 0 | 0 | 0 | 0 | 532 | 534
|  |  | Raita | 1 | 141 | Twin ACSR Moose | - | - |  | CSPTCL | CSPTCL | 0 | 0 | 0 | 0 | 0 | 0 | 532 | 534
|  |  | Raita | 2 | 141 | Twin ACSR Moose | - | - |  | CSPTCL | CSPTCL | 0 | 0 | 0 | 0 | 0 | 0 | 532 | 534
|  | Total |  |  |  |  | - |  | - |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 536 | 538
94 | MB Power | MB Power | Jabalpur (PS) | 1 | 246 | Triple ACSR Snowbird | - | - | 1x125 | WRTS-2 | WRTS-2 | 0 | 0 | 0 | 0 | 0 | 0 | 536 | 538
|  |  | Jabalpur (PS) | 2 | 246 | Triple ACSR Snowbird | - | - |  | WRTS-2 | WRTS-2 | 0 | 0 | 0 | 0 | 0 | 0 | 536 | 538
|  | Total |  |  |  |  | - |  | 125 |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 539 | 541
95 | MCCPL | ACBIL | Bilaspur | 1 | 45 | Twin ACSR Moose | - | - | - | WRTS-1 | WRTS-1 | 0 | 0 | 0 | 0 | 0 | 0 | 539 | 541
|  |  | ACBIL | 1 | 16 | Twin ACSR Moose | - | - |  | WRTS-1 | ACBIL | 0 | 0 | 0 | 0 | 0 | 0 | 539 | 541
|  | Total |  |  |  |  | - |  | - |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 542 | 544
96 | Mouda | NTPC | Wardha | 1 | 124 | Quad ACSR Moose | - | - | 1x80 | WRTS-1 | WRTS-1 | 0 | 0 | 0 | 0 | 0 | 0 | 542 | 544
|  |  | Wardha | 2 | 124 | Quad ACSR Moose | - | - |  | WRTS-1 | WRTS-1 | 0 | 0 | 0 | 0 | 0 | 0 | 542 | 544
|  | Total |  |  |  |  | - |  | 80 |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 545 | 547
97 | Nagda | MPPTCL | Dehgam | 1 | 331 | Twin ACSR Moose | 50 | - | 2X50 | WRTS-2 | WRTS-2 | 0 | 1 | 0 | 0 | 0 | 0 | 545 | 547
|  |  | Dehgam | 2 | 331 | Twin ACSR Moose | 50 | - |  | WRTS-2 | WRTS-2 | 0 | 1 | 0 | 0 | 0 | 0 | 545 | 547
|  |  | Shujalpur | 1 | 202 | Twin ACSR Moose | - | - |  | WRTS-2 | WRTS-2 | 0 | 0 | 0 | 0 | 0 | 0 | 545 | 547
|  |  | Shujalpur | 2 | 152 | Twin ACSR Moose | - | - |  | WRTS-2 | WRTS-2 | 0 | 0 | 0 | 0 | 0 | 0 | 545 | 547
|  |  | Indira Sagar | 1 | 188 | Twin ACSR Moose | - | - |  | MPPTCL | MPPTCL | 0 | 0 | 0 | 0 | 0 | 0 | 545 | 547
|  |  | Indore-MP | 1 | 108 | Twin ACSR Moose | - | - |  | MPPTCL | MPPTCL | 0 | 0 | 0 | 0 | 0 | 0 | 545 | 547
|  |  | Rajgarh | 1 | 104 | Twin ACSR Moose | 50 | - |  | WRTS-2 | WRTS-2 | 0 | 1 | 0 | 0 | 0 | 0 | 545 | 547
|  |  | Rajgarh | 2 | 104 | Twin ACSR Moose | 50 | - |  | WRTS-2 | WRTS-2 | 0 | 1 | 0 | 0 | 0 | 0 | 545 | 547
|  | Total |  |  |  |  | 200 |  | 100 |  |  | 0 | 4 | 0 | 0 | 0 | 0 | 554 | 556
98 | Nagothane | MSETCL | Padghe | 1 | 116 | Twin ACSR Moose | - | - | 1X80 | MSETCL | MSETCL | 0 | 0 | 0 | 0 | 0 | 0 | 554 | 556
|  |  | Padghe | 2 | 116 | Twin ACSR Moose | - | - |  | MSETCL | MSETCL | 0 | 0 | 0 | 0 | 0 | 0 | 554 | 556
|  |  | RGPPL | 1 | 136 | Twin ACSR Moose | - | - |  | MSETCL | RGPPL | 0 | 0 | 0 | 0 | 0 | 0 | 554 | 556
|  |  | RGPPL | 2 | 136 | Twin ACSR Moose | - | - |  | MSETCL | RGPPL | 0 | 0 | 0 | 0 | 0 | 0 | 554 | 556
|  | Total |  |  |  |  | - |  | 80 |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 559 | 561
99 | Nanded | MSETCL | Chandrapur-II | 1 | 257 | Twin ACSR Moose | - | - | - |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 559 | 561
|  |  | Parli-M | 1 | 163 | Twin ACSR Moose | - | - |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 559 | 561
|  | Total |  |  |  |  | - |  | - |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 562 | 564
100 | Nandgaonpeth | Rattan India | Koradi-II | 1 | 140 | Twin ACSR Moose | - | - | 1x80 | MSETCL | MSETCL | 0 | 0 | 0 | 0 | 0 | 0 | 562 | 564
|  |  | Akola | 1 | 117 | Twin ACSR Moose | - | - |  | MSETCL | MSETCL | 0 | 0 | 0 | 0 | 0 | 0 | 562 | 564
|  |  | Akola(2) | 1 | 104 | Twin ACSR Moose | - | - |  | MEGPTL | MEGPTL | 0 | 0 | 0 | 0 | 0 | 0 | 562 | 564
|  |  | Akola(2) | 2 | 104 | Twin ACSR Moose | - | - |  | MEGPTL | MEGPTL | 0 | 0 | 0 | 0 | 0 | 0 | 562 | 564
|  | Total |  |  |  |  | - |  | 80 |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 567 | 569
101 | Navsari | PGCIL | DGEN | 1 | 105 | Twin ACSR Moose | - | - | 1X63 | TPL | DGEN | 0 | 0 | 0 | 0 | 0 | 0 | 567 | 569
|  |  | DGEN | 2 | 105 | Twin ACSR Moose | - | - |  | TPL | DGEN | 0 | 0 | 0 | 0 | 0 | 0 | 567 | 569
|  |  | Gandhar | 1 | 106 | Twin ACSR Moose | - | - |  | WRTS-2 | NTPC | 0 | 0 | 0 | 0 | 0 | 0 | 567 | 569
|  |  | Magarawada | 1 | 126 | Twin ACSR Moose | - | - |  | WRTS-2 | WRTS-2 | 0 | 0 | 0 | 0 | 0 | 0 | 567 | 569
|  |  | Magarawada | 2 | 126 | Twin ACSR Moose | - | - |  | WRTS-2 | WRTS-2 | 0 | 0 | 0 | 0 | 0 | 0 | 567 | 569
|  |  | Ukai | 1 | 83 | Twin ACSR Moose | - | - |  | GETCO | GETCO | 0 | 0 | 0 | 0 | 0 | 0 | 567 | 569
|  | Total |  |  |  |  | - |  | 63 |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 574 | 576
102 | New koyna | MSETCL | Jaigad | 1 | 55 | Twin ACSR Moose | - | - | - | MSETCL | JAIGAD-IPP | 0 | 0 | 0 | 0 | 0 | 0 | 574 | 576
|  |  | Jaigad | 2 | 55 | Twin ACSR Moose | - | - |  | MSETCL | JAIGAD-IPP | 0 | 0 | 0 | 0 | 0 | 0 | 574 | 576
|  |  | Karad | 1 | 72 | Twin ACSR Moose | - | - |  | MSETCL | MSETCL | 0 | 0 | 0 | 0 | 0 | 0 | 574 | 576
|  |  | Karad | 2 | 72 | Twin ACSR Moose | - | - |  | MSETCL | MSETCL | 0 | 0 | 0 | 0 | 0 | 0 | 574 | 576
|  |  | Koyna stage-IV | 1 | 14 | Twin ACSR Moose | - | - |  | MSETCL | MSETCL | 0 | 0 | 0 | 0 | 0 | 0 | 574 | 576
|  |  | Koyna stage-IV | 2 | 14 | Twin ACSR Moose | - | - |  | MSETCL | MSETCL | 0 | 0 | 0 | 0 | 0 | 0 | 574 | 576
|  |  | RGPPL | 1 | 60 | Twin ACSR Moose | - | - |  | MSETCL | RGPPL | 0 | 0 | 0 | 0 | 0 | 0 | 574 | 576
|  |  | RGPPL | 2 | 60 | Twin ACSR Moose | - | - |  | MSETCL | RGPPL | 0 | 0 | 0 | 0 | 0 | 0 | 574 | 576
|  | Total |  |  |  |  | - |  | - |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 583 | 585
103 | NSPCL | NSPCL | Raipur | 1 | 14 | Twin ACSR Moose | - | - | - | NSPCL | WRTS-1 | 0 | 0 | 0 | 0 | 0 | 0 | 583 | 585
|  |  | Raipur | 2 | 14 | Twin ACSR Moose | - | - |  | NSPCL | WRTS-1 | 0 | 0 | 0 | 0 | 0 | 0 | 583 | 585
|  | Total |  |  |  |  | - |  | - |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 586 | 588
104 | Padghe | MSETCL | Boisar | 1 | 101 | Twin ACSR Moose | 50 | - | 1X80 | WRTS-2 | WRTS-2 | 0 | 1 | 0 | 0 | 0 | 0 | 586 | 588
|  |  | Nagothane | 1 | 116 | Twin ACSR Moose | - | - |  | MSETCL | MSETCL | 0 | 0 | 0 | 0 | 0 | 0 | 586 | 588
|  |  | Nagothane | 2 | 116 | Twin ACSR Moose | - | - |  | MSETCL | MSETCL | 0 | 0 | 0 | 0 | 0 | 0 | 586 | 588
|  |  | Pune-PG | 1 | 96 | Twin ACSR Moose | - | - |  | MSETCL | WRTS-1 | 0 | 0 | 0 | 0 | 0 | 0 | 586 | 588
|  |  | Bableshwar | 1 | 174 | Twin ACSR Moose | - | - |  | MSETCL | MSETCL | 0 | 0 | 0 | 0 | 0 | 0 | 586 | 588
|  |  | Bableshwar | 2 | 174 | Twin ACSR Moose | - | - |  | MSETCL | MSETCL | 0 | 0 | 0 | 0 | 0 | 0 | 586 | 588
|  |  | Kalwa | 1 | 72 | Twin ACSR Moose | - | - |  | MSETCL | MSETCL | 0 | 0 | 0 | 0 | 0 | 0 | 586 | 588
|  |  | Kalwa | 2 | 72 | Twin ACSR Moose | - | - |  | MSETCL | MSETCL | 0 | 0 | 0 | 0 | 0 | 0 | 586 | 588
|  |  | Kharghar | 1 | 85 | Twin ACSR Moose | - | - |  | MSETCL | MSETCL | 0 | 0 | 0 | 0 | 0 | 0 | 586 | 588
|  |  | Tarapur-3&4 | 1 | 91 | Twin ACSR Moose | - | - |  | WRTS-1 | NPCIL | 0 | 0 | 0 | 0 | 0 | 0 | 586 | 588
|  |  | Tarapur-3&4 | 2 | 91 | Twin ACSR Moose | - | - |  | WRTS-1 | NPCIL | 0 | 0 | 0 | 0 | 0 | 0 | 586 | 588
|  | Total |  |  |  |  | 50 |  | 80 |  |  | 0 | 1 | 0 | 0 | 0 | 0 | 598 | 600
105 | Parli-M | MSETCL | Lonikhand-II | 1 | 284 | Twin ACSR Moose | 50 | - | 1X50 | MSETCL | MSETCL | 0 | 1 | 0 | 0 | 0 | 0 | 598 | 600
|  |  | Lonikhand-II | 2 | 284 | Twin ACSR Moose | 50 | - |  | MSETCL | MSETCL | 0 | 1 | 0 | 0 | 0 | 0 | 598 | 600
|  |  | Sholapur-M | 1 | 182 | Twin ACSR Moose | 50 | - |  | MSETCL | MSETCL | 0 | 1 | 0 | 0 | 0 | 0 | 598 | 600
|  |  | Chandrapur-II | 1 | 357 | Twin ACSR Moose | 50 | - |  | MSETCL | MSETCL | 0 | 1 | 0 | 0 | 0 | 0 | 598 | 600
|  |  | Nanded | 1 | 163 | Twin ACSR Moose | 50 | - |  | MSETCL | MSETCL | 0 | 1 | 0 | 0 | 0 | 0 | 598 | 600
|  |  | Parli-PG | 1 | 5 | Twin ACSR Moose | - | - |  | WRTS-1 | WRTS-1 | 0 | 0 | 0 | 0 | 0 | 0 | 598 | 600
|  |  | Parli-PG | 2 | 5 | Twin ACSR Moose | - | - |  | WRTS-1 | WRTS-1 | 0 | 0 | 0 | 0 | 0 | 0 | 598 | 600
|  |  | Chandrapur | 3 | 371 | Twin ACSR Moose | 50 | - |  | MSETCL | MSETCL | 0 | 1 | 0 | 0 | 0 | 0 | 598 | 600
|  | Total |  |  |  |  | 300 |  | 50 |  |  | 0 | 6 | 0 | 0 | 0 | 0 | 607 | 609
106 | Parli-PG | PGCIL | Pune-PG (Shikrapur) | 1 | 272 | Twin ACSR Moose | 50 | - | 1X63 + 1X125 | WRTMPL/WRTS-1 | WRTS-1 | 0 | 1 | 0 | 0 | 0 | 0 | 607 | 609
|  |  | Pune-PG (Shikrapur) | 2 | 272 | Twin ACSR Moose | 50 | - |  | WRTMPL/WRTS-1 | WRTS-1 | 0 | 1 | 0 | 0 | 0 | 0 | 607 | 609
|  |  | Sholapur-PG | 1 | 65 | Twin ACSR Moose | - | - |  | WRTMPL/WRTS-1 | WRTS-1 | 0 | 0 | 0 | 0 | 0 | 0 | 607 | 609
|  |  | Sholapur-PG | 2 | 65 | Twin ACSR Moose | - | - |  | WRTMPL/WRTS-1 | WRTS-1 | 0 | 0 | 0 | 0 | 0 | 0 | 607 | 609
|  |  | Bhadrawati | 1 | 388 | Twin ACSR Moose | 63 | - |  | WRTS-1 | WRTS-1 | 0 | 0 | 0 | 1 | 0 | 0 | 607 | 609
|  |  | Dhariwal | 1 | 390 | Twin ACSR Moose | 63 | - |  | WRTS-1 | Dhariwal Infra | 0 | 0 | 0 | 1 | 0 | 0 | 607 | 609
|  |  | Parli-M | 1 | 5 | Twin ACSR Moose | - | - |  | WRTS-1 | MSETCL | 0 | 0 | 0 | 0 | 0 | 0 | 607 | 609
|  |  | Parli-M | 2 | 5 | Twin ACSR Moose | - | - |  | WRTS-1 | MSETCL | 0 | 0 | 0 | 0 | 0 | 0 | 607 | 609
|  |  | Wardha | 1 | 337 | Quad ACSR Moose | 63 | - |  | WRTS-1 | WRTS-1 | 0 | 0 | 0 | 1 | 0 | 0 | 607 | 609
|  |  | Wardha | 2 | 337 | Quad ACSR Moose | 63 | - |  | WRTS-1 | WRTS-1 | 0 | 0 | 0 | 1 | 0 | 0 | 607 | 609
|  | Total |  |  |  |  | 352 |  | 188 |  |  | 0 | 2 | 0 | 4 | 0 | 0 | 618 | 620
107 | Pathadi | LANCO | Bilaspur-PS | 1 | 31 | Twin ACSR Moose | - | - | - | LANCO | WRTS-1 | 0 | 0 | 0 | 0 | 0 | 0 | 618 | 620
|  |  | Bilaspur-PS | 2 | 31 | Twin ACSR Moose | - | - |  | LANCO | WRTS-1 | 0 | 0 | 0 | 0 | 0 | 0 | 618 | 620
|  | Total |  |  |  |  | - |  | - |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 621 | 623
18 | Pirana-PG | PGCIL | Dehgam | 1 | 56 | Twin ACSR Moose | - | - | 1X125 | WRTS-2 | WRTS-2 | 0 | 0 | 0 | 0 | 0 | 0 | 621 | 623
|  |  | Dehgam | 2 | 56 | Twin ACSR Moose | - | - |  | WRTS-2 | WRTS-2 | 0 | 0 | 0 | 0 | 0 | 0 | 621 | 623
|  |  | Pirana-T | 1 | 6 | Twin ACSR Moose | - | - |  | TPL | TPL | 0 | 0 | 0 | 0 | 0 | 0 | 621 | 623
|  |  | Pirana-T | 2 | 6 | Twin ACSR Moose | - | - |  | TPL | TPL | 0 | 0 | 0 | 0 | 0 | 0 | 621 | 623
|  |  | Vadodara-PS | 1 | 131 | Quad ACSR Moose | - | - |  | WRTS-2 | WRTS-2 | 0 | 0 | 0 | 0 | 0 | 0 | 621 | 623
|  |  | Vadodara-PS | 2 | 131 | Quad ACSR Moose | - | - |  | WRTS-2 | WRTS-2 | 0 | 0 | 0 | 0 | 0 | 0 | 621 | 623
|  | Total |  |  |  |  | - |  | 1x125 |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 628 | 630
109 | Pirana-T | TPL | Pirana-PG | 1 | 6 | Twin ACSR Moose | - | - | - | TPL | WRTS-2 | 0 | 0 | 0 | 0 | 0 | 0 | 628 | 630
|  |  | Pirana-PG | 2 | 6 | Twin ACSR Moose | - | - |  | TPL | WRTS-2 | 0 | 0 | 0 | 0 | 0 | 0 | 628 | 630
|  |  | Sugen | 1 | 212 | Twin ACSR Moose | 50 | - |  | TPL | TPL | 0 | 1 | 0 | 0 | 0 | 0 | 628 | 630
|  |  | Uno-Sugen | 1 | 209 | Twin ACSR Moose | 50 | - |  | TPL | TPL | 0 | 1 | 0 | 0 | 0 | 0 | 628 | 630
|  | Total |  |  |  |  | 100 |  | - |  |  | 0 | 2 | 0 | 0 | 0 | 0 | 633 | 635
110 | Pithampur | MPPTCL | Indore-PG | 1 | 150 | Twin ACSR Moose | - | - | 1x50 | MPPTCL | MPPTCL | 0 | 0 | 0 | 0 | 0 | 0 | 633 | 635
|  |  | Indore-PG | 2 | 150 | Twin ACSR Moose | - | - |  | MPPTCL | MPPTCL | 0 | 0 | 0 | 0 | 0 | 0 | 633 | 635
|  |  | Malwa | 1 | 136 | Twin ACSR Moose | - | - |  | MPPTCL | MPPTCL | 0 | 0 | 0 | 0 | 0 | 0 | 633 | 635
|  |  | Malwa | 2 | 136 | Twin ACSR Moose | - | - |  | MPPTCL | MPPTCL | 0 | 0 | 0 | 0 | 0 | 0 | 633 | 635
|  | Total |  |  |  |  | - |  | 50 |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 638 | 640
111 | Pune-PG | PGCIL | Chakan | 1 | 18 | Twin ACSR Moose | - | - | 1x50 | WRTS-1 | MSETCL | 0 | 0 | 0 | 0 | 0 | 0 | 638 | 640
|  |  | Kalwa | 1 | 104 | Twin ACSR Moose | - | - |  | MSETCL | MSETCL | 0 | 0 | 0 | 0 | 0 | 0 | 638 | 640
|  |  | Lonikhand | 1 | 40 | Twin ACSR Moose | - | - |  | MSETCL | MSETCL | 0 | 0 | 0 | 0 | 0 | 0 | 638 | 640
|  |  | Padghe | 1 | 96 | Twin ACSR Moose | - | - |  | MSETCL | MSETCL | 0 | 0 | 0 | 0 | 0 | 0 | 638 | 640
|  |  | Pune-PG(Shikrapur) | 1 | 64 | Twin ACSR Moose | 50 | Yes |  | WRTMPL/WRTS-1 | WRTS-1 | 1 | 0 | 0 | 0 | 0 | 0 | 638 | 640
|  |  | Pune-PG(Shikrapur) | 2 | 64 | Twin ACSR Moose | 50 | Yes |  | WRTMPL/WRTS-1 | WRTS-1 | 1 | 0 | 0 | 0 | 0 | 0 | 638 | 640
|  |  | Pune-PG(Shikrapur) | 2 | 64 | Twin ACSR Moose | 50 | Yes |  | WRTMPL/WRTS-1 | WRTS-1 | 1 | 0 | 0 | 0 | 0 | 0 | 638 | 640
|  |  | Pune-PG(Shikrapur) | 2 | 64 | Twin ACSR Moose | 50 | Yes |  | WRTMPL/WRTS-1 | WRTS-1 | 1 | 0 | 0 | 0 | 0 | 0 | 638 | 640
|  | Total |  |  |  |  | 300 |  | 50 |  |  | 4 | 0 | 0 | 0 | 0 | 0 | 647 | 649
112 | Pune-PG(Shikrapur) | PGCIL | Pune-PG | 1 | 64 | Twin ACSR Moose | - | - | - | WRTMPL/WRTS-1 | WRTS-1 | 0 | 0 | 0 | 0 | 0 | 0 | 647 | 649
|  |  | Pune-PG | 2 | 64 | Twin ACSR Moose | - | - |  | WRTMPL/WRTS-1 | WRTS-1 | 0 | 0 | 0 | 0 | 0 | 0 | 647 | 649
|  |  | Pune-PG | 3 | 64 | Twin ACSR Moose | - | - |  | WRTMPL/WRTS-1 | WRTS-1 | 0 | 0 | 0 | 0 | 0 | 0 | 647 | 649
|  |  | Pune-PG | 4 | 64 | Twin ACSR Moose | - | - |  | WRTS-1 | WRTS-1 | 0 | 0 | 0 | 0 | 0 | 0 | 647 | 649
|  |  | Aurangabad-M(Waluj) | 1 | 315 | Twin ACSR Moose | 50 | Yes |  | WRTMPL | MSETCL | 1 | 0 | 0 | 0 | 0 | 0 | 647 | 649
|  |  | Aurangabad-M(Waluj) | 2 | 315 | Twin ACSR Moose | 50 | Yes |  | WRTMPL | MSETCL | 1 | 0 | 0 | 0 | 0 | 0 | 647 | 649
|  |  | Parli-PG | 1 | 272 | Twin ACSR Moose | 50 | - |  | WRTMPL/WRTS-1 | WRTS-1 | 0 | 1 | 0 | 0 | 0 | 0 | 647 | 649
|  |  | Parli-PG | 2 | 272 | Twin ACSR Moose | 50 | - |  | WRTMPL/WRTS-1 | WRTS-1 | 0 | 1 | 0 | 0 | 0 | 0 | 647 | 649
|  | Total |  |  |  |  | 200 |  | - |  |  | 2 | 2 | 0 | 0 | 0 | 0 | 656 | 658
113 | Raigarh | PGCIL | India Bharath | 1 | 110 | Twin ACSR Moose | - | - | 1X63 + 1X125 | WRTS-1/ERTS-2 | ERTS-2 | 0 | 0 | 0 | 0 | 0 | 0 | 656 | 658
|  |  | Jharsuguda | 2 | 125 | Twin ACSR Moose | - | - |  | WRTS-1/ERTS-2 | ERTS-2 | 0 | 0 | 0 | 0 | 0 | 0 | 656 | 658
|  |  | Rourkela | 1 | 130 | Twin ACSR Moose | - | - |  | WRTS-1/ERTS-2 | ERTS-2 | 0 | 0 | 0 | 0 | 0 | 0 | 656 | 658
|  |  | Sterlite | 2 | 130 | Twin ACSR Moose | - | - |  | WRTS-1/ERTS-2 | ERTS-2 | 0 | 0 | 0 | 0 | 0 | 0 | 656 | 658
|  |  | Raipur | 1 | 217 | Twin ACSR Moose | - | - |  | WRTS-1 | WRTS-1 | 0 | 0 | 0 | 0 | 0 | 0 | 656 | 658
|  |  | Raipur | 2 | 217 | Twin ACSR Moose | - | - |  | WRTS-1 | KWPCL | 0 | 0 | 0 | 0 | 0 | 0 | 656 | 658
|  |  | Raigarh-PS(Kotra) | 1 | 7 | Twin ACSR Moose | - | - |  | WRTS-1 | WRTS-1 | 0 | 0 | 0 | 0 | 0 | 0 | 656 | 658
|  |  | Raigarh-PS(Kotra) | 2 | 7 | Twin ACSR Moose | - | - |  | WRTS-1 | WRTS-1 | 0 | 0 | 0 | 0 | 0 | 0 | 656 | 658
|  |  | KSK | 1 | 119 | Twin ACSR Moose | - | - |  | WRTS-1 | KSK | 0 | 0 | 0 | 0 | 0 | 0 | 656 | 658
|  |  | RKM | 1 | 6 | Twin ACSR Moose | - | - |  | WRTS-1 | RKMPPL | 0 | 0 | 0 | 0 | 0 | 0 | 656 | 658
|  | Total |  |  |  |  | - |  | 188 |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 667 | 669
114 | Raigarh-PS(Kotra) | PGCIL | Athena | 1 | 25 | Quad ACSR Moose | - | - | 1X80 | ACPL | ACPL | 0 | 0 | 0 | 0 | 0 | 0 | 667 | 669
|  |  | Athena | 2 | 25 | Quad ACSR Moose | - | - |  | ACPL | ACPL | 0 | 0 | 0 | 0 | 0 | 0 | 667 | 669
|  |  | DB-Power | 1 | 18 | Twin ACSR Moose | - | - |  | DB-Power | DB-Power | 0 | 0 | 0 | 0 | 0 | 0 | 667 | 669
|  |  | DB-Power | 2 | 18 | Twin ACSR Moose | - | - |  | DB-Power | DB-Power | 0 | 0 | 0 | 0 | 0 | 0 | 667 | 669
|  |  | KWPCL | 1 | 19 | Twin ACSR Moose | - | - |  | KWPCL | KWPCL | 0 | 0 | 0 | 0 | 0 | 0 | 667 | 669
|  |  | KWPCL | 2 | 19 | Twin ACSR Moose | - | - |  | KWPCL | KWPCL | 0 | 0 | 0 | 0 | 0 | 0 | 667 | 669
|  |  | Lara | 1 | 18 | Twin ACSR Moose | - | - |  | WRTS-1 | NTPC | 0 | 0 | 0 | 0 | 0 | 0 | 667 | 669
|  |  | Lara | 2 | 18 | Twin ACSR Moose | - | - |  | WRTS-1 | NTPC | 0 | 0 | 0 | 0 | 0 | 0 | 667 | 669
|  |  | Raigarh | 1 | 7 | Twin ACSR Moose | - | - |  | WRTS-1 | WRTS-1 | 0 | 0 | 0 | 0 | 0 | 0 | 667 | 669
|  |  | Raigarh | 2 | 7 | Twin ACSR Moose | - | - |  | WRTS-1 | WRTS-1 | 0 | 0 | 0 | 0 | 0 | 0 | 667 | 669
|  |  | SKS | 1 | 28 | Twin ACSR Moose | - | - |  | WRTS-1 | SKS | 0 | 0 | 0 | 0 | 0 | 0 | 667 | 669
|  |  | SKS | 2 | 28 | Twin ACSR Moose | - | - |  | WRTS-1 | SKS | 0 | 0 | 0 | 0 | 0 | 0 | 667 | 669
|  | Total |  |  |  |  | - |  | 80 |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 680 | 682
115 | Raipur | PGCIL | Wardha | 1 | 371 | Quad ACSR Moose | 63 | - | 1X125 + 1X80 | WRTS-1 | WRTS-1 | 0 | 0 | 0 | 1 | 0 | 0 | 680 | 682
|  |  | Wardha | 2 | 371 | Quad ACSR Moose | 63 | - |  | WRTS-1 | WRTS-1 | 0 | 0 | 0 | 1 | 0 | 0 | 680 | 682
|  |  | Raipur-PS(Durg) | 1 | 22 | Twin ACSR Moose | - | - |  | WRTS-1 | WRTS-1 | 0 | 0 | 0 | 0 | 0 | 0 | 680 | 682
|  |  | Raipur-PS(Durg) | 2 | 22 | Twin ACSR Moose | - | - |  | WRTS-1 | WRTS-1 | 0 | 0 | 0 | 0 | 0 | 0 | 680 | 682
|  |  | Bhadrawati | 1 | 333 | Twin ACSR Moose | 80 | - |  | WRTS-1 | WRTS-1 | 0 | 0 | 0 | 0 | 0 | 1 | 680 | 682
|  |  | Bhadrawati | 2 | 346 | Twin ACSR Moose | 50 | Yes |  | WRTS-1 | WRTS-1 | 1 | 0 | 0 | 0 | 0 | 0 | 680 | 682
|  |  | Bhadrawati | 3 | 346 | Twin ACSR Moose | 63 | - |  | WRTS-1 | WRTS-1 | 0 | 0 | 0 | 1 | 0 | 0 | 680 | 682
|  |  | Bhilai | 1 | 13 | Twin ACSR Moose | - | - |  | WRTS-1 | CSPTCL | 0 | 0 | 0 | 0 | 0 | 0 | 680 | 682
|  |  | JPL | 1 | 258 | Twin ACSR Moose | 50 | - |  | JPL | JPL | 0 | 1 | 0 | 0 | 0 | 0 | 680 | 682
|  |  | JPL | 2 | 258 | Twin ACSR Moose | 50 | - |  | JPL | JPL | 0 | 1 | 0 | 0 | 0 | 0 | 680 | 682
|  |  | Korba-NTPC | 1 | 212 | Twin ACSR Moose | 63 | - |  | WRTS-1 | NTPC | 0 | 0 | 0 | 1 | 0 | 0 | 680 | 682
|  |  | Korba-NTPC | 2 | 212 | Twin ACSR Moose | 63 | - |  | WRTS-1 | NTPC | 0 | 0 | 0 | 1 | 0 | 0 | 680 | 682
|  |  | KSK Mahanadi | 1 | 147 | Twin ACSR Moose | 50 | - |  | WRTS-1 | KSK | 0 | 1 | 0 | 0 | 0 | 0 | 680 | 682
|  |  | KSK Mahanadi | 2 | 150 | Twin ACSR Moose | 50 | - |  | WRTS-1 | KSK | 0 | 1 | 0 | 0 | 0 | 0 | 680 | 682
|  |  | NSPCL | 1 | 14 | Twin ACSR Moose | - | - |  | NSPCL | NSPCL | 0 | 0 | 0 | 0 | 0 | 0 | 680 | 682
|  |  | NSPCL | 2 | 14 | Twin ACSR Moose | - | - |  | NSPCL | NSPCL | 0 | 0 | 0 | 0 | 0 | 0 | 680 | 682
|  |  | Raigarh | 1 | 217 | Twin ACSR Moose | 63 | - |  | WRTS-1 | WRTS-1 | 0 | 0 | 0 | 1 | 0 | 0 | 680 | 682
|  |  | Raigarh | 1 | 217 | Twin ACSR Moose | 63 | - |  | WRTS-1 | WRTS-1 | 0 | 0 | 0 | 1 | 0 | 0 | 680 | 682
|  | Total |  |  |  |  | 771 |  | 205 |  |  | 1 | 4 | 0 | 7 | 0 | 1 | 699 | 701
116 | Raipur-PS(Durg) | PGCIL | GMR-CG | 1 | 65 | Twin ACSR Moose | - | - | - | GMR | GMR-CG | 0 | 0 | 0 | 0 | 0 | 0 | 699 | 701
|  |  | GMR-CG | 2 | 65 | Twin ACSR Moose | - | - |  | GMR | GMR-CG | 0 | 0 | 0 | 0 | 0 | 0 | 699 | 701
|  |  | Raipur | 1 | 22 | Twin ACSR Moose | - | - |  | WRTS-1 | WRTS-1 | 0 | 0 | 0 | 0 | 0 | 0 | 699 | 701
|  |  | Raipur | 2 | 22 | Twin ACSR Moose | - | - |  | WRTS-1 | WRTS-1 | 0 | 0 | 0 | 0 | 0 | 0 | 699 | 701
|  | Total |  |  |  |  | - |  | - |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 704 | 706
117 | Raita | CSPTCL | Marwa | 1 | 141 | Twin ACSR Moose | - | - | - | CSPTCL | CSPTCL | 0 | 0 | 0 | 0 | 0 | 0 | 704 | 706
|  |  | Marwa | 2 | 141 | Twin ACSR Moose | - | - |  | CSPTCL | CSPTCL | 0 | 0 | 0 | 0 | 0 | 0 | 704 | 706
|  |  | Bhilai | 1 | 56 | Twin ACSR Moose | - | - |  | CSPTCL | CSPTCL | 0 | 0 | 0 | 0 | 0 | 0 | 704 | 706
|  |  | Bhilai | 2 | 56 | Twin ACSR Moose | - | - |  | CSPTCL | CSPTCL | 0 | 0 | 0 | 0 | 0 | 0 | 704 | 706
|  |  | Bhilai | 3 | 56 | Twin ACSR Moose | - | - |  | CSPTCL | CSPTCL | 0 | 0 | 0 | 0 | 0 | 0 | 704 | 706
|  |  | Korba (W) | 1 | 144 | Twin ACSR Moose | - | - |  | CSPTCL | CSPTCL | 0 | 0 | 0 | 0 | 0 | 0 | 704 | 706
|  | Total |  |  |  |  | - |  | - |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 711 | 713
118 | Rajgarh | PGCIL | Nagda | 1 | 104 | Twin ACSR Moose | - | - | 1X125 | WRTS-2 | MPPTCL | 0 | 0 | 0 | 0 | 0 | 0 | 711 | 713
|  |  | Nagda | 2 | 104 | Twin ACSR Moose | - | - |  | WRTS-2 | MPPTCL | 0 | 0 | 0 | 0 | 0 | 0 | 711 | 713
|  |  | Kasor | 1 | 243 | Twin ACSR Moose | - | - |  | WRTGPL | GETCO | 0 | 0 | 0 | 0 | 0 | 0 | 711 | 713
|  |  | Kasor | 2 | 243 | Twin ACSR Moose | - | - |  | WRTGPL | GETCO | 0 | 0 | 0 | 0 | 0 | 0 | 711 | 713
|  |  | Khandwa | 1 | 221 | Twin ACSR Moose | - | - |  | WRTS-2 | WRTS-2 | 0 | 0 | 0 | 0 | 0 | 0 | 711 | 713
|  |  | Khandwa | 2 | 221 | Twin ACSR Moose | - | - |  | WRTS-2 | WRTS-2 | 0 | 0 | 0 | 0 | 0 | 0 | 711 | 713
|  |  | SSP | 1 | 178 | Twin ACSR Moose | - | - |  | MPPTCL | SSNNL | 0 | 0 | 0 | 0 | 0 | 0 | 711 | 713
|  |  | SSP | 2 | 178 | Twin ACSR Moose | - | - |  | MPPTCL | SSNNL | 0 | 0 | 0 | 0 | 0 | 0 | 711 | 713
|  | Total |  |  |  |  | - |  | 125 |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 720 | 722
119 | Ranchodpura | GETCO | Zerda(Kansari) | 1 | 140 | Twin ACSR Moose | - | - | 1X50 + 1X125 | WRTGPL | GETCO | 0 | 0 | 0 | 0 | 0 | 0 | 720 | 722
|  |  | Zerda(Kansari) | 2 | 140 | Twin ACSR Moose | - | - |  | WRTGPL | GETCO | 0 | 0 | 0 | 0 | 0 | 0 | 720 | 722
|  |  | Chorania | 1 | 103 | Twin ACSR Moose | - | - |  | WRTGPL | GETCO | 0 | 0 | 0 | 0 | 0 | 0 | 720 | 722
|  |  | Chorania | 2 | 103 | Twin ACSR Moose | - | - |  | WRTGPL | GETCO | 0 | 0 | 0 | 0 | 0 | 0 | 720 | 722
|  |  | Bachau | 1 | 282 | Triple ACSR Snowbird | 50 | - |  | WRTS-2 | WRTS-2 | 0 | 1 | 0 | 0 | 0 | 0 | 720 | 722
|  |  | Bachau | 2 | 282 | Triple ACSR Snowbird | 50 | - |  | WRTS-2 | WRTS-2 | 0 | 1 | 0 | 0 | 0 | 0 | 720 | 722
|  |  | Dehgam | 1 | 62 | Twin ACSR Moose | - | - |  | WRTS-2 | WRTS-2 | 0 | 0 | 0 | 0 | 0 | 0 | 720 | 722
|  |  | Dehgam | 2 | 62 | Twin ACSR Moose | - | - |  | WRTS-2 | WRTS-2 | 0 | 0 | 0 | 0 | 0 | 0 | 720 | 722
|  | Total |  |  |  |  | 100 |  | 175 |  |  | 0 | 2 | 0 | 0 | 0 | 0 | 729 | 731
120 | RGPPL | RGPPL | New Koyna | 1 | 60 | Twin ACSR Moose | - | - | - | MSETCL | MSETCL | 0 | 0 | 0 | 0 | 0 | 0 | 729 | 731
|  |  | New Koyna | 2 | 60 | Twin ACSR Moose | - | - |  | MSETCL | MSETCL | 0 | 0 | 0 | 0 | 0 | 0 | 729 | 731
|  |  | Nagothane | 1 | 136 | Twin ACSR Moose | - | - |  | MSETCL | MSETCL | 0 | 0 | 0 | 0 | 0 | 0 | 729 | 731
|  |  | Nagothane | 2 | 136 | Twin ACSR Moose | - | - |  | MSETCL | MSETCL | 0 | 0 | 0 | 0 | 0 | 0 | 729 | 731
|  | Total |  |  |  |  | - |  | - |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 734 | 736
121 | RKM | RKM | Raigarh | 1 | 6 | Twin ACSR Moose | - | - | 2x50 | WRTS-1 | WRTS-1 | 0 | 0 | 0 | 0 | 0 | 0 | 734 | 736
|  |  | KSK Mahanadi | 1 | 104 | Twin ACSR Moose | - | - |  | WRTS-1 | KSK | 0 | 0 | 0 | 0 | 0 | 0 | 734 | 736
|  | Total |  |  |  |  | - |  | 100 |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 737 | 739
122 | Sami | APL | APL-Mundra | 1 | 282 | Twin ACSR Moose | 50 | - | 1x50 | ATIL | APL | 0 | 1 | 0 | 0 | 0 | 0 | 737 | 739
|  |  | APL-Mundra | 2 | 282 | Twin ACSR Moose | 50 | - |  | ATIL | APL | 0 | 1 | 0 | 0 | 0 | 0 | 737 | 739
|  |  | Dehgam | 1 | 152 | Twin ACSR Moose | - | - |  | ATIL | WRTS-2 | 0 | 0 | 0 | 0 | 0 | 0 | 737 | 739
|  |  | Dehgam | 2 | 152 | Twin ACSR Moose | - | - |  | ATIL | WRTS-2 | 0 | 0 | 0 | 0 | 0 | 0 | 737 | 739
|  | Total |  |  |  |  | 100 |  | 50 |  |  | 0 | 2 | 0 | 0 | 0 | 0 | 742 | 744
123 | Sasan | SPL | Jabalpur | 1 | 340 | Twin ACSR Moose | 50 | - | - | WRTS-2 | WRTS-2 | 0 | 1 | 0 | 0 | 0 | 0 | 742 | 744
|  |  | Vindhyachal | 3 | 20 | Twin ACSR Moose | - | - |  | WRTS-2 | NTPC | 0 | 0 | 0 | 0 | 0 | 0 | 742 | 744
|  |  | Vindhyachal-PS | 1 | 8 | Twin ACSR Moose | - | - |  | WRTS-2 | NTPC | 0 | 0 | 0 | 0 | 0 | 0 | 742 | 744
|  |  | Vindhyachal-PS | 2 | 8 | Twin ACSR Moose | - | - |  | WRTS-2 | WRTS-2 | 0 | 0 | 0 | 0 | 0 | 0 | 742 | 744
|  | Total |  |  |  |  | 50 |  | - |  |  | 0 | 1 | 0 | 0 | 0 | 0 | 747 | 749
124 | Satna | PGCIL | Bina-PG | 1 | 276 | Twin ACSR Moose | 50 | - | 1X50 + 1X63 | WRTS-2 | WRTS-2 | 0 | 1 | 0 | 0 | 0 | 0 | 747 | 749
|  |  | Bina-PG | 2 | 276 | Twin ACSR Moose | 50 | - |  | WRTS-2 | WRTS-2 | 0 | 1 | 0 | 0 | 0 | 0 | 747 | 749
|  |  | Bina-NTS | 3 | 272 | Twin ACSR Moose | 50 | - |  | WRTS-2 | WRTS-2 | 0 | 1 | 0 | 0 | 0 | 0 | 747 | 749
|  |  | Bina-PG | 4 | 273 | Twin ACSR Moose | 50 | - |  | WRTS-2 | WRTS-2 | 0 | 1 | 0 | 0 | 0 | 0 | 747 | 749
|  |  | JP-Nigrie | 1 | 161 | Twin ACSR Moose | - | - |  | Jaypee | Jaypee | 0 | 0 | 0 | 0 | 0 | 0 | 747 | 749
|  |  | JP-Nigrie | 2 | 161 | Twin ACSR Moose | - | - |  | Jaypee | Jaypee | 0 | 0 | 0 | 0 | 0 | 0 | 747 | 749
|  |  | Vindhyachal | 1 | 267 | Twin ACSR Moose | 50 | - |  | WRTS-2 | NTPC | 0 | 1 | 0 | 0 | 0 | 0 | 747 | 749
|  |  | Vindhyachal | 2 | 267 | Twin ACSR Moose | 50 | - |  | WRTS-2 | NTPC | 0 | 1 | 0 | 0 | 0 | 0 | 747 | 749
|  |  | Vindhyachal | 3 | 258 | Twin ACSR Moose | 50 | - |  | WRTS-2 | NTPC | 0 | 1 | 0 | 0 | 0 | 0 | 747 | 749
|  |  | Vindhyachal | 4 | 258 | Twin ACSR Moose | 50 | - |  | WRTS-2 | NTPC | 0 | 1 | 0 | 0 | 0 | 0 | 747 | 749
|  | Total |  |  |  |  | 400 |  | 113 |  |  | 0 | 8 | 0 | 0 | 0 | 0 | 758 | 760
125 | Satpura | MPPTCL | Indira sagar | 1 | 189 | Twin ACSR Moose | - | - | 2X63 | MPPTCL | MPPTCL | 0 | 0 | 0 | 0 | 0 | 0 | 758 | 760
|  |  | Itarsi | 1 | 79 | Twin ACSR Moose | - | - |  | WRTS-2 | WRTS-2 | 0 | 0 | 0 | 0 | 0 | 0 | 758 | 760
|  |  | Astha | 1 | 240 | Twin ACSR Moose | - | - |  | MPPTCL | MPPTCL | 0 | 0 | 0 | 0 | 0 | 0 | 758 | 760
|  |  | Astha | 2 | 240 | Twin ACSR Moose | - | - |  | MPPTCL | MPPTCL | 0 | 0 | 0 | 0 | 0 | 0 | 758 | 760
|  |  | Koradi | 1 | 149 | Twin ACSR Moose | 50 | - |  | WRTS-1 | MSETCL | 0 | 1 | 0 | 0 | 0 | 0 | 758 | 760
|  |  | Seoni | 1 | 156 | Twin ACSR Moose | - | - |  | WRTS-1 | WRTS-1 | 0 | 0 | 0 | 0 | 0 | 0 | 758 | 760
|  | Total |  |  |  |  | 50 |  | 126 |  |  | 0 | 1 | 0 | 0 | 0 | 0 | 765 | 767
126 | Seoni | PGCIL | Satpura | 1 | 156 | Twin ACSR Moose | 50 | - | 2x125 | WRTS-1 | MPPTCL | 0 | 1 | 0 | 0 | 0 | 0 | 765 | 767
|  |  | Khandwa | 1 | 352 | Quad AAAC Moose | 80 | - |  | WRTS-1 | WRTS-2 | 0 | 0 | 0 | 0 | 0 | 1 | 765 | 767
|  |  | Khandwa | 2 | 352 | Quad AAAC Moose | 80 | - |  | WRTS-1 | WRTS-2 | 0 | 0 | 0 | 0 | 0 | 1 | 765 | 767
|  |  | Bhilai | 1 | 230 | Twin ACSR Moose | - | - |  | WRTS-1 | CSPTCL | 0 | 0 | 0 | 0 | 0 | 0 | 765 | 767
|  | Total |  |  |  |  | 210 |  | 250 |  |  | 0 | 1 | 0 | 0 | 0 | 2 | 770 | 772
127 | Sholapur-M | MSETCL | Sholapur -PG | 1 | 178 | Twin ACSR Moose | - | - | - | MSETCL | WRTS-1 | 0 | 0 | 0 | 0 | 0 | 0 | 770 | 772
|  |  | Parli-M | 1 | 182 | Twin ACSR Moose | - | - |  | MSETCL | MSETCL | 0 | 0 | 0 | 0 | 0 | 0 | 770 | 772
|  | Total |  |  |  |  | - |  | - |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 773 | 775
128 | Shujalpur | PGCIL | Bina-PG | 1 | 200 | Twin ACSR Moose | 50 | - | 1X63 + 1X125 | WRTS-2 | WRST-2 | 0 | 1 | 0 | 0 | 0 | 0 | 773 | 775
|  |  | Bina-PG | 2 | 200 | Twin ACSR Moose | 50 | - |  | WRTS-2 | WRST-2 | 0 | 1 | 0 | 0 | 0 | 0 | 773 | 775
|  |  | Nagda | 1 | 202 | Twin ACSR Moose | 63 | Yes |  | WRTS-2 | MPPTCL | 0 | 0 | 1 | 0 | 0 | 0 | 773 | 775
|  |  | Nagda | 2 | 152 | Twin ACSR Moose | 63 | Yes |  | WRTS-2 | MPPTCL | 0 | 0 | 1 | 0 | 0 | 0 | 773 | 775
|  |  | RAPP | 1 | 201 | Twin ACSR Moose | 50 | - |  |  |  | 0 | 1 | 0 | 0 | 0 | 0 | 773 | 775
|  |  | RAPP | 2 | 201 | Twin ACSR Moose | 50 | - |  |  |  | 0 | 1 | 0 | 0 | 0 | 0 | 773 | 775
|  | Total |  |  |  |  | 326 |  | 188 |  |  | 0 | 4 | 2 | 0 | 0 | 0 | 780 | 782
129 | Sipat | NTPC | Raipur | 1 | 149 | Twin ACSR Moose | - | - | - | WRTS-1 | WRTS-1 | 0 | 0 | 0 | 0 | 0 | 0 | 780 | 782
|  |  | Raipur | 2 | 149 | Twin ACSR Moose | - | - |  | WRTS-1 | WRTS-1 | 0 | 0 | 0 | 0 | 0 | 0 | 780 | 782
|  |  | Raipur | 3 | 149 | Twin ACSR Moose | - | - |  | WRTS-1 | WRTS-1 | 0 | 0 | 0 | 0 | 0 | 0 | 780 | 782
|  |  | Ranchi | 1 | 405 | Twin ACSR Moose | 80 | - |  | WRTS-1/ERTS-1 | ERTS-1 | 0 | 0 | 0 | 0 | 0 | 1 | 780 | 782
|  |  | Ranchi | 2 | 405 | Twin ACSR Moose | 80 | - |  | WRTS-1/ERTS-1 | ERTS-1 | 0 | 0 | 0 | 0 | 0 | 1 | 780 | 782
|  |  | Korba-NTPC | 1 | 100 | Twin ACSR Moose | - | - |  | WRTS-1 | NTPC | 0 | 0 | 0 | 0 | 0 | 0 | 780 | 782
|  | Total |  |  |  |  | 160 |  | - |  |  | 0 | 0 | 0 | 0 | 0 | 2 | 787 | 789
130 | SKS | SKS | Raigarh-PS(Kotra) | 1 | 28 | Twin ACSR Moose | - | - | 1x50 | WRTS-1 | WRTS-1 | 0 | 0 | 0 | 0 | 0 | 0 | 787 | 789
|  |  | Raigarh-PS(Kotra) | 2 | 28 | Twin ACSR Moose | - | - |  | WRTS-1 | WRTS-1 | 0 | 0 | 0 | 0 | 0 | 0 | 787 | 789
|  | Total | [6 empty] | 50 |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 790 | 792
131 | Soja | GETCO | Wanakbori | 1 | 95 | Twin ACSR Moose | - | - | 1X50 + 1X80 | GETCO | GETCO | 0 | 0 | 0 | 0 | 0 | 0 | 790 | 792
|  |  | Dehgam | 1 | 41 | Twin ACSR Moose | - | - |  | WRTS-2 | WRTS-2 | 0 | 0 | 0 | 0 | 0 | 0 | 790 | 792
|  |  | Zerda | 1 | 135 | Twin ACSR Moose | - | - |  | GETCO | GETCO | 0 | 0 | 0 | 0 | 0 | 0 | 790 | 792
|  | Total |  |  |  |  | - |  | 130 |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 794 | 796
132 | Solapur-NTPC | NTPC | Solapur-PG | 1 | 11 | Twin ACSR Moose | - | - | - | WRTS-1 | NTPC | 0 | 0 | 0 | 0 | 0 | 0 | 794 | 796
|  |  | Solapur-PG | 2 | 11 | Twin ACSR Moose | - | - |  | WRTS-1 | NTPC | 0 | 0 | 0 | 0 | 0 | 0 | 794 | 796
|  | Total |  |  |  |  | - |  | - |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 797 | 799
133 | Solapur-PG | PGCIL | Solapur-NTPC | 1 | 11 | Twin ACSR Moose | - | - | 1X63 | WRTS-1 | WRTS-1 | 0 | 0 | 0 | 0 | 0 | 0 | 797 | 799
|  |  | Solapur-NTPC | 2 | 11 | Twin ACSR Moose | - | - |  | WRTS-1 | WRTS-1 | 0 | 0 | 0 | 0 | 0 | 0 | 797 | 799
|  |  | Karad | 1 | 299 | Twin ACSR Moose | 80 | Yes |  | WRTMPL/MSETCL | MSETCL | 0 | 0 | 0 | 0 | 1 | 0 | 797 | 799
|  |  | Kolhapur | 1 | 220 | Twin ACSR Moose | 50 | - |  | WRTMPL | MSETCL | 0 | 1 | 0 | 0 | 0 | 0 | 797 | 799
|  |  | Kolhapur | 2 | 220 | Twin ACSR Moose | 50 | - |  | WRTMPL | MSETCL | 0 | 1 | 0 | 0 | 0 | 0 | 797 | 799
|  |  | Parli-PG | 1 | 65 | Twin ACSR Moose | - | - |  | WRTMPL/WRTS-1 | WRTS-1 | 0 | 0 | 0 | 0 | 0 | 0 | 797 | 799
|  |  | Parli-PG | 2 | 65 | Twin ACSR Moose | - | - |  | WRTMPL/WRTS-1 | WRTS-1 | 0 | 0 | 0 | 0 | 0 | 0 | 797 | 799
|  |  | Sholapur-M | 1 | 178 | Twin ACSR Moose | - | - |  | MSETCL | MSETCL | 0 | 0 | 0 | 0 | 0 | 0 | 797 | 799
|  | Total |  |  |  |  | 180 |  | 63 |  |  | 0 | 2 | 0 | 0 | 1 | 0 | 806 | 808
124 | SSP | SSNL | Dhule | 1 | 236 | Twin ACSR Moose | - | - | - | MSETCL | MSETCL | 0 | 0 | 0 | 0 | 0 | 0 | 806 | 808
|  |  | Dhule | 2 | 236 | Twin ACSR Moose | - | - |  | MSETCL | MSETCL | 0 | 0 | 0 | 0 | 0 | 0 | 806 | 808
|  |  | Asoj | 1 | 83 | Twin ACSR Moose | - | - |  | GETCO | GETCO | 0 | 0 | 0 | 0 | 0 | 0 | 806 | 808
|  |  | Rajgarh | 1 | 178 | Twin ACSR Moose | - | - |  | MPPTCL | MPPTCL | 0 | 0 | 0 | 0 | 0 | 0 | 806 | 808
|  |  | Rajgarh | 2 | 178 | Twin ACSR Moose | - | - |  | MPPTCL | MPPTCL | 0 | 0 | 0 | 0 | 0 | 0 | 806 | 808
|  |  | Kasor | 1 | 146 | Twin ACSR Moose | - | - |  | GETCO | GETCO | 0 | 0 | 0 | 0 | 0 | 0 | 806 | 808
|  | Total |  |  |  |  | - |  | - |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 813 | 815
135 | Sugen | TPL | Uno-Sugen | 1 | 3 | Twin ACSR Moose | - | - | - | TPL | TPL | 0 | 0 | 0 | 0 | 0 | 0 | 813 | 815
|  |  | Pirana-T | 1 | 212 | Twin ACSR Moose | - | - |  | TPL | TPL | 0 | 0 | 0 | 0 | 0 | 0 | 813 | 815
|  |  | Pirana-T | 1 | 209 | Twin ACSR Moose | - | - |  | TPL | TPL | 0 | 0 | 0 | 0 | 0 | 0 | 813 | 815
|  |  | Gandhar | 1 | 64 | Twin ACSR Moose | - | - |  | WRTS-2 | NTPC | 0 | 0 | 0 | 0 | 0 | 0 | 813 | 815
|  |  | Sugen | 1 | 3 | Twin ACSR Moose | - | - |  | TPL | TPL | 0 | 0 | 0 | 0 | 0 | 0 | 813 | 815
|  |  | Vapi | 1 | 118 | Twin ACSR Moose | - | - |  | WRTS-2 | WRTS-2 | 0 | 0 | 0 | 0 | 0 | 0 | 813 | 815
|  | Total |  |  |  |  | - |  | - |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 820 | 822
136 | Tamnar-PS | PGCIL | JPL_extn(Tamnar) | 1 | 10 | Twin ACSR Moose | - | - | - |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 820 | 822
|  |  | JPL_extn(Tamnar) | 2 | 10 | Twin ACSR Moose | - | - |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 820 | 822
|  |  | JPL_extn(Tamnar) | 3 | 10 | Twin ACSR Moose | - | - |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 820 | 822
|  |  | JPL_extn(Tamnar) | 3 | 10 | Twin ACSR Moose | - | - |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 820 | 822
|  |  | TRN | 1 | 15 | Twin ACSR Moose | - | - |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 820 | 822
|  |  | TRN | 2 | 15 | Twin ACSR Moose | - | - |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 820 | 822
|  | Total |  |  |  |  | - |  | - |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 827 | 829
137 | Taptithanda | MEGPTCL | Deepnagar | 1 | 203 | Twin ACSR Moose | - | - | - | MSETCL | MSETCL | 0 | 0 | 0 | 0 | 0 | 0 | 827 | 829
|  |  | Ektuni (Aurangabad(3)) | 1 | 5.36 | Twin ACSR Moose | - | - |  | MSETCL | MSETCL | 0 | 0 | 0 | 0 | 0 | 0 | 827 | 829
|  |  | Aurangabad-M(Waluj) | 1 | 135 | Twin ACSR Moose | - | - |  | MSETCL | MSETCL | 0 | 0 | 0 | 0 | 0 | 0 | 827 | 829
|  | Total |  |  |  |  | - |  | - |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 831 | 833
138 | Tarapur-3&4 | NPCIL | Padghe | 1 | 91 | Twin ACSR Moose | - | - | - | WRTS-1 | MSETCL | 0 | 0 | 0 | 0 | 0 | 0 | 831 | 833
|  |  | Padghe | 2 | 91 | Twin ACSR Moose | - | - |  | WRTS-1 | MSETCL | 0 | 0 | 0 | 0 | 0 | 0 | 831 | 833
|  |  | Boisar | 1 | 21 | Twin ACSR Moose | - | - |  | WRTS-2 | WRTS-2 | 0 | 0 | 0 | 0 | 0 | 0 | 831 | 833
|  |  | Boisar | 2 | 21 | Twin ACSR Moose | - | - |  | WRTS-2 | WRTS-2 | 0 | 0 | 0 | 0 | 0 | 0 | 831 | 833
|  | Total |  |  |  |  | - |  | - |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 836 | 838
139 | Tiroda | MEGPTCL | Warora | 1 | 219 | Twin ACSR Moose | - | - | 2X80 | MEGPTL | MEGPTL | 0 | 0 | 0 | 0 | 0 | 0 | 836 | 838
|  |  | Warora | 2 | 219 | Twin ACSR Moose | - | - |  | MEGPTL | MEGPTL | 0 | 0 | 0 | 0 | 0 | 0 | 836 | 838
|  | Total |  |  |  |  | - |  | 160 |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 839 | 841
140 | TRN | TRN | Tamnar-PS | 1 | 15 | Twin ACSR Moose | - | - | - | WRTS-1 | WRTS-1 | 0 | 0 | 0 | 0 | 0 | 0 | 839 | 841
|  |  | Tamnar-PS | 2 | 15 | Twin ACSR Moose | - | - |  | WRTS-1 | WRTS-1 | 0 | 0 | 0 | 0 | 0 | 0 | 839 | 841
|  | Total |  |  |  |  | - |  | - |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 842 | 844
141 | Ukai | TPL | Kosamba | 1 | 81 | Twin ACSR Moose | - | - | - | GETCO | GETCO | 0 | 0 | 0 | 0 | 0 | 0 | 842 | 844
|  |  | Kosamba | 2 | 68 | Twin ACSR Moose | - | - |  | GETCO | GETCO | 0 | 0 | 0 | 0 | 0 | 0 | 842 | 844
|  |  | Navsari | 1 | 83 | Twin ACSR Moose | - | - |  | GETCO | WRTS-2 | 0 | 0 | 0 | 0 | 0 | 0 | 842 | 844
|  | Total |  |  |  |  | - |  | - |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 846 | 848
142 | Uno-Sugen | TPL | Pirana-T | 1 | 209 | Twin ACSR Moose | - | - | 1x80 | TPL | TPL | 0 | 0 | 0 | 0 | 0 | 0 | 846 | 848
|  |  | Sugen | 1 | 3 | Twin ACSR Moose | - | - |  | TPL | TPL | 0 | 0 | 0 | 0 | 0 | 0 | 846 | 848
|  | Total |  |  |  |  | - |  | 80 |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 849 | 851
143 | Vadinar | Essar | Hadala | 1 | 113 | Twin ACSR Moose | - | - | - | GETCO | GETCO | 0 | 0 | 0 | 0 | 0 | 0 | 849 | 851
|  |  | Hadala | 2 | 113 | Twin ACSR Moose | - | - |  | GETCO | GETCO | 0 | 0 | 0 | 0 | 0 | 0 | 849 | 851
|  |  | Bachau | 1 | 226 | Twin ACSR Moose | - | - |  | WRTS-2 | WRTS-2 | 0 | 0 | 0 | 0 | 0 | 0 | 849 | 851
|  |  | Bachau | 2 | 226 | Twin ACSR Moose | - | - |  | WRTS-2 | WRTS-2 | 0 | 0 | 0 | 0 | 0 | 0 | 849 | 851
|  | Total |  |  |  |  | - |  | - |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 854 | 856
144 | Vadodara-PS | PGCIL | Pirana-PG | 1 | 131 | Quad ACSR Moose | - | - | - | WRTS-2 | WRTS-2 | 0 | 0 | 0 | 0 | 0 | 0 | 854 | 856
|  |  | Pirana-PG | 2 | 131 | Quad ACSR Moose | - | - |  | WRTS-2 | WRTS-2 | 0 | 0 | 0 | 0 | 0 | 0 | 854 | 856
|  |  | Asoj | 1 | 14 | Quad ACSR Moose | - | - |  | WRTS-2 | GETCO | 0 | 0 | 0 | 0 | 0 | 0 | 854 | 856
|  |  | Asoj | 2 | 14 | Quad ACSR Moose | - | - |  | WRTS-2 | GETCO | 0 | 0 | 0 | 0 | 0 | 0 | 854 | 856
|  | Total |  |  |  |  | - |  | - |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 859 | 861
145 | Vandana | Vandana Vidyut | Birsingpur | 1 | 215 | Twin ACSR Moose | 50 | - | - | WRTS-2 | MPPTCL | 0 | 1 | 0 | 0 | 0 | 0 | 859 | 861
|  |  | Korba-NTPC | 1 | 18 | Twin ACSR Moose | - | - |  | WRTS-2 | NTPC | 0 | 0 | 0 | 0 | 0 | 0 | 859 | 861
|  | Total |  |  |  |  | 50 |  | - |  |  | 0 | 1 | 0 | 0 | 0 | 0 | 862 | 864
146 | Vapi | PGCIL | Boisar | 1 | 91 | Twin ACSR Moose | - | - | - | WRTS-2 | WRTS-2 | 0 | 0 | 0 | 0 | 0 | 0 | 862 | 864
|  |  | Sugen | 1 | 118 | Twin ACSR Moose | - | - |  | WRTS-2 | TPL | 0 | 0 | 0 | 0 | 0 | 0 | 862 | 864
|  |  | Kala | 1 | 49 | Twin ACSR Moose | - | - |  | WRTS-2 | WRTS-2 | 0 | 0 | 0 | 0 | 0 | 0 | 862 | 864
|  |  | Kala | 2 | 52 | Twin ACSR Moose | - | - |  | WRTS-2 | WRTS-2 | 0 | 0 | 0 | 0 | 0 | 0 | 862 | 864
|  | Total |  |  |  |  | - |  | - |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 867 | 869
147 | Varsana | GETCO | APL-Mundra | 1 | 84 | Twin ACSR Moose | - | - | 1X50 + 1X125 | GETCO | APL | 0 | 0 | 0 | 0 | 0 | 0 | 867 | 869
|  |  | APL-Mundra | 2 | 84 | Twin ACSR Moose | - | - |  | GETCO | APL | 0 | 0 | 0 | 0 | 0 | 0 | 867 | 869
|  |  | Bachau | 1 | 10 | Twin ACSR Moose | - | - |  | WRTS-2 | WRTS-2 | 0 | 0 | 0 | 0 | 0 | 0 | 867 | 869
|  |  | Bachau | 2 | 10 | Twin ACSR Moose | - | - |  | WRTS-2 | WRTS-2 | 0 | 0 | 0 | 0 | 0 | 0 | 867 | 869
|  |  | Hadala | 1 | 159 | Twin ACSR Moose | - | - |  | GETCO | GETCO | 0 | 0 | 0 | 0 | 0 | 0 | 867 | 869
|  |  | Zerda(Kansari) | 1 | 258 | Twin ACSR Moose | - | - |  | GETCO | GETCO | 0 | 0 | 0 | 0 | 0 | 0 | 867 | 869
|  | Total |  |  |  |  | - |  | 175 |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 874 | 876
148 | Vindhyachal | NTPC | Jabalpur | 1 | 360 | Twin ACSR Moose | 63 | - | 1X63 + 1X50 | WRTS-2 | WRTS-2 | 0 | 0 | 0 | 1 | 0 | 0 | 874 | 876
|  |  | Jabalpur | 2 | 360 | Twin ACSR Moose | 63 | - |  | WRTS-2 | WRTS-2 | 0 | 0 | 0 | 1 | 0 | 0 | 874 | 876
|  |  | Jabalpur | 4 | 389 | Twin ACSR Moose | 63 | - |  | WRTS-2 | WRTS-2 | 0 | 0 | 0 | 1 | 0 | 0 | 874 | 876
|  |  | Satna | 1 | 267 | Twin ACSR Moose | 50 | - |  | WRTS-2 | WRTS-2 | 0 | 1 | 0 | 0 | 0 | 0 | 874 | 876
|  |  | Satna | 2 | 267 | Twin ACSR Moose | 50 | - |  | WRTS-2 | WRTS-2 | 0 | 1 | 0 | 0 | 0 | 0 | 874 | 876
|  |  | Satna | 3 | 258 | Twin ACSR Moose | 50 | - |  | WRTS-2 | WRTS-2 | 0 | 1 | 0 | 0 | 0 | 0 | 874 | 876
|  |  | Satna | 4 | 258 | Twin ACSR Moose | 50 | - |  | WRTS-2 | WRTS-2 | 0 | 1 | 0 | 0 | 0 | 0 | 874 | 876
|  |  | Sasan | 3 | 20 | Twin ACSR Moose | 63 | Yes |  | WRTS-2 | SPL | 0 | 0 | 1 | 0 | 0 | 0 | 874 | 876
|  |  | Mahan | 1 | 41 | Twin ACSR Moose | 50 | - |  | WRTS-2 | Mahan | 0 | 1 | 0 | 0 | 0 | 0 | 874 | 876
|  |  | Korba-NTPC | 2 | 289 | Twin ACSR Moose | 50 | - |  | WRTS-1 | NTPC | 0 | 1 | 0 | 0 | 0 | 0 | 874 | 876
|  |  | Vindhyachal-III | 1 | 4 | Quad ACSR Moose | - | - |  | NTPC | NTPC | 0 | 0 | 0 | 0 | 0 | 0 | 874 | 876
|  |  | Vindhyachal-III | 2 | 4 | Quad ACSR Moose | - | - |  | NTPC | NTPC | 0 | 0 | 0 | 0 | 0 | 0 | 874 | 876
|  | Total |  |  |  |  | 552 |  | 113 |  |  | 0 | 6 | 1 | 3 | 0 | 0 | 887 | 889
149 | Vindhyachal-III | NTPC | Vindhyachal-V | 1 | 4 | Quad ACSR Moose | - | - | - | NTPC | NTPC | 0 | 0 | 0 | 0 | 0 | 0 | 887 | 889
|  |  | Vindhyachal-V | 2 | 4 | Quad ACSR Moose | - | - |  | NTPC | NTPC | 0 | 0 | 0 | 0 | 0 | 0 | 887 | 889
|  |  | Vindhyachal | 1 | 4 | Quad ACSR Moose | - | - |  | NTPC | NTPC | 0 | 0 | 0 | 0 | 0 | 0 | 887 | 889
|  |  | Vindhyachal | 2 | 4 | Quad ACSR Moose | - | - |  | NTPC | NTPC | 0 | 0 | 0 | 0 | 0 | 0 | 887 | 889
|  | Total |  |  |  |  | - |  | - |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 892 | 894
150 | Vindhyachal-IV | NTPC | Vindhyachal-V | 1 | 4 | Quad ACSR Moose | - | - | 1X80 | NTPC | NTPC | 0 | 0 | 0 | 0 | 0 | 0 | 892 | 894
|  |  | Vindhyachal-V | 2 | 4 | Quad ACSR Moose | - | - |  | NTPC | NTPC | 0 | 0 | 0 | 0 | 0 | 0 | 892 | 894
|  |  | Vindhyachal-PS | 1 | 31 | Twin ACSR Moose | - | - |  | WRTS-2 | WRTS-2 | 0 | 0 | 0 | 0 | 0 | 0 | 892 | 894
|  |  | Vindhyachal-PS | 2 | 31 | Twin ACSR Moose | - | - |  | WRTS-2 | WRTS-2 | 0 | 0 | 0 | 0 | 0 | 0 | 892 | 894
|  | Total | [6 empty] | 80 |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 897 | 899
151 | Vindhyachal-PS | PGCIL | Sasan | 1 | 8 | Twin ACSR Moose | - | - | 1X63 | WRTS-2 | SPL | 0 | 0 | 0 | 0 | 0 | 0 | 897 | 899
|  |  | Sasan | 2 | 8 | Twin ACSR Moose | - | - |  | WRTS-2 | SPL | 0 | 0 | 0 | 0 | 0 | 0 | 897 | 899
|  |  | Rihand | 1 | 35 | Quad Bersimis | - | - |  | WRTS-2/NRTS-1 | NRTS-1 | 0 | 0 | 0 | 0 | 0 | 0 | 897 | 899
|  |  | Rihand | 2 | 28 | Quad Bersimis | - | - |  | WRTS-2/NRTS-1 | NRTS-1 | 0 | 0 | 0 | 0 | 0 | 0 | 897 | 899
|  |  | Vindhyachal-IV | 1 | 31 | Twin ACSR Moose | - | - |  | WRTS-2 | NTPC | 0 | 0 | 0 | 0 | 0 | 0 | 897 | 899
|  |  | Vindhyachal-IV | 2 | 31 | Twin ACSR Moose | - | - |  | WRTS-2 | NTPC | 0 | 0 | 0 | 0 | 0 | 0 | 897 | 899
|  | Total |  |  |  |  | - |  | 63 |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 904 | 906
152 | Vindhyachal-V | NTPC | Vindhyachal-IV | 1 | 4 | Quad ACSR Moose | - | - | 1x125 | NTPC | NTPC | 0 | 0 | 0 | 0 | 0 | 0 | 904 | 906
|  |  | Vindhyachal-IV | 2 | 4 | Quad ACSR Moose | - | - |  | NTPC | NTPC | 0 | 0 | 0 | 0 | 0 | 0 | 904 | 906
|  |  | Vindhyachal-III | 1 | 4 | Quad ACSR Moose | - | - |  | NTPC | NTPC | 0 | 0 | 0 | 0 | 0 | 0 | 904 | 906
|  |  | Vindhyachal-III | 2 | 4 | Quad ACSR Moose | - | - |  | NTPC | NTPC | 0 | 0 | 0 | 0 | 0 | 0 | 904 | 906
|  | Total |  |  |  |  | - |  | 125 |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 909 | 911
153 | Wanakbori | GSECL | Asoj | 1 | 76 | Twin ACSR Moose | - | - | - | GETCO | GETCO | 0 | 0 | 0 | 0 | 0 | 0 | 909 | 911
|  |  | Dehgam | 1 | 68 | Twin ACSR Moose | - | - |  | WRTS-2 | WRTS-2 | 0 | 0 | 0 | 0 | 0 | 0 | 909 | 911
|  |  | Soja | 1 | 95 | Twin ACSR Moose | - | - |  | GETCO | GETCO | 0 | 0 | 0 | 0 | 0 | 0 | 909 | 911
|  | Total |  |  |  |  | - |  | - |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 913 | 915
154 | Wardha | PGCIL | Parli-PG | 1 | 337 | Quad ACSR Moose | 63 | - | 1X50 | WRTS-1 | WRTS-1 | 0 | 0 | 0 | 1 | 0 | 0 | 913 | 915
|  |  | Parli-PG | 2 | 337 | Quad ACSR Moose | 63 | - |  | WRTS-1 | WRTS-1 | 0 | 0 | 0 | 1 | 0 | 0 | 913 | 915
|  |  | Akola | 1 | 162 | Twin ACSR Moose | - | - |  | WRTS-1 | MSETCL | 0 | 0 | 0 | 0 | 0 | 0 | 913 | 915
|  |  | Akola | 2 | 162 | Twin ACSR Moose | - | - |  | WRTS-1 | MSETCL | 0 | 0 | 0 | 0 | 0 | 0 | 913 | 915
|  |  | Mouda | 1 | 124 | Quad ACSR Moose | - | - |  | WRTS-1 | NTPC | 0 | 0 | 0 | 0 | 0 | 0 | 913 | 915
|  |  | Mouda | 2 | 124 | Quad ACSR Moose | - | - |  | WRTS-1 | NTPC | 0 | 0 | 0 | 0 | 0 | 0 | 913 | 915
|  |  | Warora | 1 | 76 | Twin ACSR Moose | - | - |  | WRTS-1 | MEGPTL | 0 | 0 | 0 | 0 | 0 | 0 | 913 | 915
|  |  | Koradi-II | 1 | 67 | Quad ACSR Moose | - | - |  | WRTS-1 | IEPL | 0 | 0 | 0 | 0 | 0 | 0 | 913 | 915
|  |  | Raipur | 1 | 371 | Quad ACSR Moose | 63 | - |  | WRTS-1 | WRTS-1 | 0 | 0 | 0 | 1 | 0 | 0 | 913 | 915
|  |  | Raipur | 2 | 371 | Quad ACSR Moose | 63 | - |  | WRTS-1 | WRTS-1 | 0 | 0 | 0 | 1 | 0 | 0 | 913 | 915
|  | Total |  |  |  |  | 252 |  | 50 |  |  | 0 | 0 | 0 | 4 | 0 | 0 | 924 | 926
155 | Warora | MEGPTCL | Chandrapur-II | 1 | 45 | Twin ACSR Moose | - | - | 1x125 | MEGPTL | MSETCL | 0 | 0 | 0 | 0 | 0 | 0 | 924 | 926
|  |  | Chandrapur-II | 2 | 45 | Twin ACSR Moose | - | - |  | MEGPTL | MSETCL | 0 | 0 | 0 | 0 | 0 | 0 | 924 | 926
|  |  | IEPL | 1 | 150 | Twin ACSR Moose | - | - |  | WRTS-1 | IEPL | 0 | 0 | 0 | 0 | 0 | 0 | 924 | 926
|  |  | Tiroda | 1 | 219 | Twin ACSR Moose | - | - |  | MEGPTL | APML | 0 | 0 | 0 | 0 | 0 | 0 | 924 | 926
|  |  | Tiroda | 2 | 219 | Twin ACSR Moose | - | - |  | MEGPTL | APML | 0 | 0 | 0 | 0 | 0 | 0 | 924 | 926
|  |  | Wardha | 1 | 76 | Twin ACSR Moose | - | - |  | WRTS-1 | WRTS-1 | 0 | 0 | 0 | 0 | 0 | 0 | 924 | 926
|  | Total |  |  |  |  | - |  | 125 |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 931 | 933
156 | Zerda(Kansari) | GETCO | Bhinmal | 1 | 143 | Twin ACSR Moose | 50 | - | 1X50 | WRTS-2/NRTS-1 | NRTS-1 | 0 | 1 | 0 | 0 | 0 | 0 | 931 | 933
|  |  | Kankroli | 1 | 234 | Twin ACSR Moose | 50 | - |  | WRTS-2/NRTS-1 | NRTS-1 | 0 | 1 | 0 | 0 | 0 | 0 | 931 | 933
|  |  | Varsana | 1 | 258 | Twin ACSR Moose | 63 | - |  | GETCO | GETCO | 0 | 0 | 0 | 1 | 0 | 0 | 931 | 933
|  |  | APL-Mundra | 1 | 332 | Twin ACSR Moose | 63 | - |  | GETCO | APL | 0 | 0 | 0 | 1 | 0 | 0 | 931 | 933
|  |  | Ranchodpura | 1 | 140 | Twin ACSR Moose | - | - |  | WRTGPL | GETCO | 0 | 0 | 0 | 0 | 0 | 0 | 931 | 933
|  |  | Ranchodpura | 2 | 140 | Twin ACSR Moose | - | - |  | WRTGPL | GETCO | 0 | 0 | 0 | 0 | 0 | 0 | 931 | 933
|  |  | Soja | 1 | 135 | Twin ACSR Moose | - | - |  | GETCO | GETCO | 0 | 0 | 0 | 0 | 0 | 0 | 931 | 933
|  | Total |  |  |  |  | 226 |  | 50 |  |  | 0 | 2 | 0 | 2 | 0 | 0 | 939 | 941

## 1200kV Lines
Sl No | End-1 | End-2 | Id | Line Owner | End-1 Owner | End-2 Owner | Km | Conductor Type | End1 LR |  | End2 LR
[9 empty] | MVAR | S/W | MVAR | S/W
1 | Bina-NTS | Bina-NTS | 1 | PGCIL | NHPTL | NHPTL | 1.9* | Octa Bersimis | - | - | - | -

## 1200kV ICTs
Sl No | Sub-Station | ID | MVA | Voltage Ratio | Owner | Normal Tap Position | Present Tap Position
1 | Bina-NTS | 1 | 1000 | 1200/400 | PGCIL | - | -
2 | Bina-NTS | 2 | 1000 | 1200/400 | PGCIL | - | -

## 765 ICTs
Sl No | Sub-Station | Ckt ID | MVA | Voltage Ratio | Owner | Normal Tap Position | Present Tap Position
1 | Akola(2) | 1 | 1500 | 765/400 | MEGPTCL | 12 | 11 |  | 0
2 | Aurangabad-PG | 1 | 1500 | 765/400 | PGCIL | 12 | 14 |  | 0
3 | Aurangabad-PG | 2 | 1500 | 765/400 | PGCIL | 12 | 14 |  | 1
4 | Bhopal-BDTCL | 1 | 1500 | 765/400 | BDTCL | 12 | 11 |  | 0
5 | Bhopal-BDTCL | 2 | 1500 | 765/400 | BDTCL | 12 | 11 |  | 1
6 | Bilaspur | 1 | 1500 | 765/400 | PGCIL | 12 | 12 |  | 0
7 | Bilaspur | 2 | 1500 | 765/400 | PGCIL | 12 | 12 |  | 1
8 | Bilaspur | 3 | 1500 | 765/400 | PGCIL | 12 | 12 |  | 1
9 | Bina-PG | 1 | 1000 | 765/400 | PGCIL | 11 | 11 | MP | 0
10 | Bina-PG | 2 | 1000 | 765/400 | PGCIL | 11 | 11 | MP | 1
11 | Champa | 1 | 1500 | 765/400 | PGCIL | 12 | 12 |  | 0
12 | Champa | 1 | 1500 | 765/400 | PGCIL | 12 | 12 |  | 1
13 | Dharamjaygarh | 1 | 1500 | 765/400 | PGCIL | 12 | 12 |  | 0
14 | Dharamjaygarh | 2 | 1500 | 765/400 | PGCIL | 12 | 12 |  | 1
15 | Dhule-BDTCL | 1 | 1500 | 765/400 | BDTCL | 12 | 13 |  | 0
16 | Dhule-BDTCL | 2 | 1500 | 765/400 | BDTCL | 12 | 13 |  | 1
17 | Ektuni (Aurangabad(3)) | 1 | 1500 | 765/400 | MEGPTCL | 12 | 12 |  | 0
18 | Gwalior | 1 | 1500 | 765/400 | PGCIL | 12 | 12B | MP | 0
19 | Gwalior | 2 | 1500 | 765/400 | PGCIL | 12 | 12B | MP | 1
20 | Indore-PG | 1 | 1500 | 765/400 | PGCIL | 12 | 12 | MP | 0
21 | Indore-PG | 2 | 1500 | 765/400 | PGCIL | 12 | 12 | MP | 1
22 | Jabalpur-PS | 1 | 1500 | 765/400 | PGCIL | 12 | 12 | MP | 0
23 | Jabalpur-PS | 2 | 1500 | 765/400 | PGCIL | 12 | 12 | MP | 1
24 | Koradi(III) | 1 | 1500 | 765/400 | MEGPTCL | 12 | 12 |  | 0
25 | Koradi(III) | 2 | 1500 | 765/400 | MEGPTCL | 12 | 12 |  | 1
26 | Pune-PG(Shikrapur) | 1 | 1500 | 765/400 | PGCIL | 12 | 12 |  | 0
27 | Pune-PG(Shikrapur) | 2 | 1500 | 765/400 | PGCIL | 12 | 12 |  | 1
28 | Raigarh-PS(Kotra) | 1 | 1500 | 765/400 | PGCIL | 12 | 12 |  | 0
29 | Raigarh-PS(Kotra) | 2 | 1500 | 765/400 | PGCIL | 12 | 12 |  | 1
30 | Raigarh-PS(Kotra) | 3 | 1500 | 765/400 | PGCIL | 12 | 12 |  | 1
31 | Raigarh-PS(Kotra) | 4 | 1500 | 765/400 | PGCIL | 12 | 12 |  | 1
32 | Raipur-PS(Durg) | 1 | 1500 | 765/400 | PGCIL | 12 | 12 |  | 0
33 | Sasan | 1 | 1000 | 765/400 | SPL | 11 | 11 | MP | 0
34 | Sasan | 2 | 1000 | 765/400 | SPL | 11 | 11 | MP | 1
35 | Satna | 1 | 1000 | 765/400 | PGCIL | 11 | 12 | MP | 0
36 | Satna | 2 | 1000 | 765/400 | PGCIL | 11 | 12 | MP | 1
37 | Seoni | 1 | 1500 | 765/400 | PGCIL | 12 | 6 | MP | 0
38 | Seoni | 2 | 1500 | 765/400 | PGCIL | 12 | 6 | MP | 1
39 | Seoni | 3 | 1500 | 765/400 | PGCIL | 12 | 6 | MP | 1
40 | Sipat | 1 | 1000 | 765/400 | NTPC | 11 | 9 |  | 0
41 | Sipat | 2 | 1000 | 765/400 | NTPC | 11 | 9 |  | 1
42 | Solapur | 1 | 1500 | 765/400 | PGCIL | 12 | 12 |  | 0
43 | Solapur | 2 | 1500 | 765/400 | PGCIL | 12 | 12 |  | 1
44 | Tamnar | 1 | 1500 | 765/400 | PGCIL | 12 | 12 |  | 0
45 | Tamnar | 2 | 1500 | 765/400 | PGCIL | 12 | 12 |  | 1
46 | Tamnar | 3 | 1500 | 765/400 | PGCIL | 12 | 12 |  | 1
47 | Tiroda | 1 | 1500 | 765/400 | MEGPTCL | 12 | 11 |  | 0
48 | Vadodora-PS | 1 | 1500 | 765/400 | PGCIL | 12 | 12 |  | 0
49 | Vadodora-PS | 2 | 1500 | 765/400 | PGCIL | 12 | 12 |  | 1
50 | Vindhyachal-PS | 1 | 1500 | 765/400 | PGCIL | 12 | 12 | MP | 0
51 | Vindhyachal-PS | 2 | 1500 | 765/400 | PGCIL | 12 | 12 | MP | 1
52 | Wardha | 1 | 1500 | 765/400 | PGCIL | 12 | 12 |  | 0
53 | Wardha | 2 | 1500 | 765/400 | PGCIL | 12 | 12 |  | 1
54 | Wardha | 3 | 1500 | 765/400 | PGCIL | 12 | 12 |  | 1
|  | Total | 77000

## 400 ICTs
Sl No | Sub-Station | ID | MVA | Voltage Ratio | Owner | Normal Tap Position | Present Tap Position
1 | ACBIL | 1 | 200 | 400/132 | ACBIL | 9 | 9 |  | 0
2 | Akola(2) | 1 | 315 | 400/220 | MSETCL | 9b | 8 |  | 0
3 | Akola(2) | 2 | 315 | 400/220 | MSETCL | 9b | 8 |  | 1
4 | Amreli | 1 | 315 | 400/220 | GETCO | 9b | 9 |  | 0
5 | Amreli | 2 | 315 | 400/220 | GETCO | 9b | 9 |  | 1
6 | Amreli | 3 | 315 | 400/220 | GETCO | 9b | 9 | MP | 1
7 | APL-Mundra | 1 | 315 | 400/220 | APL | 9b | 9 |  | 0
8 | APL-Mundra | 2 | 315 | 400/220 | APL | 9b | 9 |  | 1
9 | Asoj | 1 | 500 | 400/220 | GETCO | 9 | 12 |  | 0
10 | Asoj | 2 | 500 | 400/220 | GETCO | 9 | 12 |  | 1
11 | Asoj | 3 | 315 | 400/220 | GETCO | 9b | 12 |  | 1
12 | Asoj | 4 | 315 | 400/220 | GETCO | 9b | 12 |  | 1
13 | Astha | 1 | 315 | 400/220 | MPPTCL | 9b | 9b |  | 0
14 | Astha | 2 | 315 | 400/220 | MPPTCL | 9b | 9b |  | 1
15 | Aurangabad-M(Waluj) | 3 | 500 | 400/220 | MSETCL | 9 | 9 |  | 0
16 | Aurangabad-M(Waluj) | 1 | 315 | 400/220 | MSETCL | 9b | 9 |  | 1
17 | Aurangabad-M(Waluj) | 2 | 315 | 400/220 | MSETCL | 9b | 9 |  | 1
18 | Aurangabad-PG | 1 | 315 | 400/220 | PGCIL | 9b | 9 |  | 0
19 | Aurangabad-PG | 2 | 315 | 400/220 | PGCIL | 9b | 9 |  | 1
20 | Bableshwar | 4 | 500 | 400/220 | MSETCL | 9 | 9 |  | 0
21 | Bableshwar | 3 | 500 | 400/220 | MSETCL | 9 | 9 |  | 1
22 | Bableshwar | 1 | 315 | 400/220 | MSETCL | 9b | 9 |  | 1
23 | Bableshwar | 2 | 315 | 400/220 | MSETCL | 9b | 9 |  | 1
24 | Bachau | 1 | 315 | 400/220 | PGCIL | 9b | 9b |  | 0
25 | Bachau | 2 | 315 | 400/220 | PGCIL | 9b | 9b |  | 1
26 | Balco | 1 | 315 | 400/220 | BALCO | 9b | 9 |  | 0
27 | Balco | 2 | 315 | 400/220 | BALCO | 9b | 9 |  | 1
28 | Balco | 3 | 315 | 400/220 | BALCO | 9b | 9 |  | 1
29 | Bhadrawati | 1 | 315 | 400/220 | PGCIL | 9b | 9b |  | 0
30 | Bhatapara | 1 | 315 | 400/220 | PGCIL | 9b | 9b |  | 0
31 | Bhatapara | 2 | 315 | 400/220 | PGCIL | 9b | 9b |  | 1
32 | Bhilai | 1 | 315 | 400/220 | PGCIL | 9b | 13 | MP | 0
33 | Bhilai | 2 | 315 | 400/220 | PGCIL | 9b | 13 | MP | 1
34 | Bhilai | 3 | 315 | 400/220 | PGCIL | 9b | 13 | MP | 1
35 | Bhopal-MP | 1 | 315 | 400/220 | MPPTCL | 9b | 9 |  | 0
36 | Bhopal-MP | 2 | 315 | 400/220 | MPPTCL | 9b | 9 | MP | 1
37 | Bhopal-MP | 3 | 315 | 400/220 | MPPTCL | 9b | 9 | MP | 1
38 | Bhusawal (Khadka) | 1 | 315 | 400/220 | MSETCL | 9b | 12 | MP | 0
39 | Bina-MP | 1 | 315 | 400/220 | MPPTCL | 9b | 9 | MP | 0
40 | Bina-MP | 2 | 315 | 400/220 | MPPTCL | 9b | 9 | MP | 1
41 | Bina-MP | 3 | 315 | 400/220 | MPPTCL | 9b | 9 |  | 1
42 | Bina-PG | 1 | 315 | 400/220 | PGCIL | 9b | 9b |  | 0
43 | Birsingpur | 1 | 500 | 400/220 | MPPTCL | 9 | 11 |  | 0
44 | Boisar | 3 | 500 | 400/220 | PGCIL | 9 | 9 |  | 0
45 | Boisar | 1 | 315 | 400/220 | PGCIL | 9b | 9 |  | 1
46 | Boisar | 2 | 315 | 400/220 | PGCIL | 9b | 9 |  | 1
47 | Chakan | 1 | 315 | 400/220 | MSETCL | 9b | 11 |  | 0
48 | Chakan | 2 | 315 | 400/220 | MSETCL | 9b | 11 |  | 1
49 | Chandrapur | 1 | 315 | 400/220 | MSETCL | 9b | 9 |  | 0
50 | Chandrapur | 2 | 315 | 400/220 | MSETCL | 9b | 9 |  | 1
51 | Chhegaon | 1 | 315 | 400/220 | MPPTCL | 9b | 9b | MP | 0
52 | Chorania | 1 | 500 | 400/220 | GETCO | 9 | 13 | MP | 0
53 | Chorania | 2 | 500 | 400/220 | GETCO | 9 | 13 |  | 1
54 | Damoh | 1 | 315 | 400/220 | PGCIL | 9b | 13 |  | 0
55 | Damoh | 2 | 315 | 400/220 | PGCIL | 9b | 13 |  | 1
56 | Deepnagar | 1 | 500 | 400/220 | MSETCL | 9 | 10 |  | 0
57 | Deepnagar | 2 | 500 | 400/220 | MSETCL | 9 | 10 |  | 1
58 | Dehgam | 1 | 315 | 400/220 | PGCIL | 9b | 12 |  | 0
59 | Dehgam | 2 | 315 | 400/220 | PGCIL | 9b | 12 |  | 1
60 | Dhule-MS | 3 | 500 | 400/220 | MSETCL | 9 | 9 |  | 0
61 | Dhule-MS | 1 | 315 | 400/220 | MSETCL | 9b | 11 |  | 1
62 | Dhule-MS | 2 | 315 | 400/220 | MSETCL | 9b | 11 |  | 1
63 | Gandhar | 1 | 500 | 400/220 | NTPC | 9b | 10 | MP | 0
64 | Gandhar | 2 | 500 | 400/220 | NTPC | 9b | 10 | MP | 1
65 | GPEC | 1 | 500 | 400/220 | GETCO | 9 | 11 | MP | 0
66 | Gwalior | 1 | 315 | 400/220 | PGCIL | 9b | 9b |  | 0
67 | Gwalior | 2 | 315 | 400/220 | PGCIL | 9b | 9b |  | 1
68 | Gwalior | 3 | 315 | 400/220 | PGCIL | 9b | 9b |  | 1
69 | Hadala | 1 | 315 | 400/220 | GETCO | 9b | 9 |  | 0
70 | Hadala | 2 | 315 | 400/220 | GETCO | 9b | 9 |  | 1
71 | Hadala | 3 | 315 | 400/220 | GETCO | 9b | 9 |  | 1
72 | Hazira | 1 | 500 | 400/220 | ESSAR | 9 | 8 | MP | 0
73 | Hazira | 2 | 500 | 400/220 | ESSAR | 9 | 8 | MP | 1
74 | Hazira | 3 | 500 | 400/220 | ESSAR | 9 | 8 | MP | 1
75 | Indore-MP | 1 | 315 | 400/220 | MPPTCL | 9b | 13 | MP | 0
76 | Indore-MP | 2 | 315 | 400/220 | MPPTCL | 9b | 13 | MP | 1
77 | Indore-MP | 3 | 315 | 400/220 | MPPTCL | 9b | 13 | MP | 1
78 | Indore-MP | 4 | 315 | 400/220 | MPPTCL | 9b | 13 | MP | 1
79 | Itarsi | 1 | 315 | 400/220 | PGCIL | 9b | 11 |  | 0
80 | Jabalpur | 1 | 315 | 400/220 | PGCIL | 9b | 11 |  | 0
81 | Jabalpur | 2 | 315 | 400/220 | PGCIL | 9b | 11 |  | 1
82 | Jejuri | 1 | 500 | 400/220 | MSETCL | 9 | 9 |  | 0
83 | Jejuri | 2 | 500 | 400/220 | MSETCL | 9 | 9 |  | 1
84 | Jetpur | 4 | 500 | 400/220 | GETCO | 9 | 9b |  | 0
85 | Jetpur | 1 | 315 | 400/220 | GETCO | 9b | 9b |  | 1
86 | Jetpur | 2 | 315 | 400/220 | GETCO | 9b | 9b |  | 1
87 | Jetpur | 3 | 315 | 400/220 | GETCO | 9b | 9b |  | 1
88 | JPL | 1 | 315 | 400/220 | JPL | 9b | 9 |  | 0
89 | JPL | 2 | 315 | 400/220 | JPL | 9b | 9 |  | 1
90 | Julwania | 1 | 315 | 400/220 | MPPTCL | 9b | 9b |  | 0
91 | Julwania | 2 | 315 | 400/220 | MPPTCL | 9b | 9b |  | 1
92 | Kala | 1 | 315 | 400/220 | PGCIL | 9b | 9b |  | 0
93 | Kala | 2 | 315 | 400/220 | PGCIL | 9b | 9b |  | 1
94 | Kalwa | 2 | 600 | 400/220 | MSETCL | 9 | 11 |  | 0
95 | Kalwa | 1 | 500 | 400/220 | MSETCL | 9 | 11 |  | 1
96 | Kalwa | 3 | 500 | 400/220 | MSETCL | 9 | 11 |  | 1
97 | Karad | 1 | 315 | 400/220 | MSETCL | 9b | 8 |  | 0
98 | Karad | 2 | 315 | 400/220 | MSETCL | 9b | 8 |  | 1
99 | Karad | 3 | 315 | 400/220 | MSETCL | 9b | 8 | MP | 1
100 | Kasor | 1 | 315 | 400/220 | GETCO | 9b | 9 | MP | 0
101 | Kasor | 2 | 315 | 400/220 | GETCO | 9b | 9 | MP | 1
102 | Katni | 1 | 315 | 400/220 | MPPTCL | 9b | 9 |  | 0
103 | Katni | 1 | 315 | 400/220 | MPPTCL | 9b | 9 |  | 1
104 | Khandwa | 1 | 315 | 400/220 | PGCIL | 9b | 11 |  | 0
105 | Khandwa | 2 | 315 | 400/220 | PGCIL | 9b | 11 |  | 1
106 | Khaparkheda | 1 | 500 | 400/220 | MSETCL | 9 | 7 |  | 0
107 | Khaparkheda | 2 | 500 | 400/220 | MSETCL | 9 | 7 |  | 1
108 | Kharghar | 2 | 500 | 400/220 | MSETCL | 9 | 11 |  | 0
109 | Kharghar | 1 | 315 | 400/220 | MSETCL | 9b | 11 |  | 1
110 | Kharghar | 3 | 315 | 400/220 | MSETCL | 9b | 11 |  | 1
111 | Kolhapur | 1 | 315 | 400/220 | MSETCL | 9b | 9 |  | 0
112 | Kolhapur | 2 | 315 | 400/220 | MSETCL | 9b | 9 |  | 1
113 | Koradi | 1 | 315 | 400/220 | MSETCL | 9b | 7 |  | 0
114 | Koradi | 2 | 315 | 400/220 | MSETCL | 9b | 7 |  | 1
115 | Koradi-II | 2 | 500 | 400/220 | MSETCL | 9 | 7 |  | 0
116 | Korba (W) | 1 | 500 | 400/220 | CSEPTCL | 9 | 12 |  | 0
117 | Kosamba | 1 | 315 | 400/220 | GETCO | 9b | 8 |  | 0
118 | Kosamba | 2 | 315 | 400/220 | GETCO | 9b | 8 |  | 1
119 | Lonikhand | 1 | 315 | 400/220 | MSETCL | 9b | 13 |  | 0
120 | Lonikhand | 2 | 315 | 400/220 | MSETCL | 9b | 13 |  | 1
121 | Lonikhand | 3 | 315 | 400/220 | MSETCL | 9b | 13 |  | 1
122 | Lonikhand-II | 1 | 500 | 400/220 | MSETCL | 9 | 9 |  | 0
123 | Lonikhand-II | 2 | 500 | 400/220 | MSETCL | 9 | 9 | MP | 1
124 | Magarawada | 1 | 315 | 400/220 | PGCIL | 9b | 9b |  | 0
125 | Magarawada | 2 | 315 | 400/220 | PGCIL | 9b | 9b |  | 1
126 | Malwa | 1 | 315 | 400/220 | MPPTCL | 9b | 9b |  | 0
127 | Mansar | 1 | 315 | 400/220 | GETCO | 9b | 9b |  | 0
128 | Mansar | 2 | 315 | 400/220 | GETCO | 9b | 9b |  | 1
129 | Mapusa | 1 | 315 | 400/220 | PGCIL | 9b | 10 |  | 0
130 | Mapusa | 2 | 315 | 400/220 | PGCIL | 9b | 10 |  | 1
131 | Mapusa | 3 | 315 | 400/220 | PGCIL | 9b | 10 |  | 1
132 | Marwa | 1 | 315 | 400/220 | CSEPTCL | 9b | 9b | MP | 0
133 | Mouda | 1 | 200 | 400/132 | NTPC | 9 | 9 | MP | 0
134 | Mouda | 2 | 200 | 400/132 | NTPC | 9 | 9 | MP | 1
135 | Nagda | 1 | 315 | 400/220 | MPPTCL | 9b | 11 |  | 0
136 | Nagda | 2 | 315 | 400/220 | MPPTCL | 9b | 11 |  | 1
137 | Nagda | 3 | 315 | 400/220 | MPPTCL | 9b | 11 |  | 1
138 | Nagothane | 3 | 500 | 400/220 | MSETCL | 9 | 8 |  | 0
139 | Nagothane | 1 | 315 | 400/220 | MSETCL | 9b | 9 |  | 1
140 | Nagothane | 2 | 315 | 400/220 | MSETCL | 9b | 9 |  | 1
141 | Nanded | 1 | 500 | 400/220 | MSETCL | 9b | 9b |  | 0
142 | Nanded | 2 | 500 | 400/220 | MSETCL | 9b | 9b |  | 1
143 | Navsari | 3 | 500 | 400/220 | PGCIL | 9 | 9 |  | 0
144 | Navsari | 1 | 315 | 400/220 | PGCIL | 9b | 9 |  | 1
145 | Navsari | 2 | 315 | 400/220 | PGCIL | 9b | 9 |  | 1
146 | New koyna | 2 | 500 | 400/220 | MSETCL | 9 | 11 |  | 0
147 | New koyna | 1 | 315 | 400/220 | MSETCL | 9b | 11 |  | 1
148 | NSPCL | 1 | 315 | 400/220 | PGCIL | 9b | 8 |  | 0
149 | NSPCL | 2 | 315 | 400/220 | PGCIL | 9b | 8 |  | 1
150 | Padghe | 4 | 600 | 400/220 | PGCIL | 9 | 8 |  | 0
151 | Padghe | 1 | 315 | 400/220 | PGCIL | 9b | 8 |  | 1
152 | Padghe | 2 | 315 | 400/220 | MSETCL | 9b | 8 |  | 1
153 | Padghe | 3 | 315 | 400/220 | MSETCL | 9b | 8 |  | 1
154 | Parli-M | 3 | 500 | 400/220 | MSETCL | 9 | 12 | MP | 0
155 | Parli-M | 1 | 315 | 400/220 | MSETCL | 9b | 12 | MP | 1
156 | Parli-M | 2 | 315 | 400/220 | MSETCL | 9b | 12 |  | 1
157 | Pirana-PG | 1 | 315 | 400/220 | PGCIL | 9b | 10 |  | 0
158 | Pirana-PG | 2 | 315 | 400/220 | PGCIL | 9b | 10 |  | 1
159 | Pirana-T | 1 | 315 | 400/132 | TPL | 9 | 9 |  | 0
160 | Pirana-T | 2 | 315 | 400/132 | TPL | 9 | 9 |  | 1
161 | Pithampur | 1 | 315 | 400/220 | MPPTCL | 9b | 9b |  | 0
162 | Pithampur | 2 | 315 | 400/220 | MPPTCL | 9b | 9b |  | 1
163 | Pune-PG | 1 | 315 | 400/220 | PGCIL | 9b | 9 |  | 0
164 | Pune-PG | 2 | 315 | 400/220 | PGCIL | 9b | 9 |  | 1
165 | Pune-PG | 3 | 315 | 400/220 | PGCIL | 9b | 9 |  | 1
166 | Raigarh | 1 | 315 | 400/220 | PGCIL | 9b | 13 | MP | 0
167 | Raigarh | 2 | 315 | 400/220 | PGCIL | 9b | 13 | MP | 1
168 | Raipur | 1 | 315 | 400/220 | PGCIL | 9b | 13 |  | 0
169 | Raipur | 2 | 315 | 400/220 | PGCIL | 9b | 13 |  | 1
170 | Raipur | 3 | 315 | 400/220 | PGCIL | 9b | 13 |  | 1
171 | Raita | 1 | 315 | 400/220 | CSEPTCL | 9b | 9 |  | 0
172 | Raita | 2 | 315 | 400/220 | CSEPTCL | 9b | 9 | MP | 1
173 | Rajgarh | 1 | 315 | 400/220 | PGCIL | 9b | 11 | MP | 0
174 | Rajgarh | 2 | 315 | 400/220 | PGCIL | 9b | 11 | MP | 1
175 | Ranchodpura | 1 | 315 | 400/220 | PGCIL | 9b | 9b | MP | 0
176 | Ranchodpura | 2 | 315 | 400/220 | PGCIL | 9b | 9b |  | 1
177 | Ranchodpura | 3 | 315 | 400/220 | PGCIL | 9b | 9b |  | 1
178 | Ranchodpura | 4 | 315 | 400/220 | PGCIL | 9b | 9b |  | 1
179 | Satna | 1 | 315 | 400/220 | PGCIL | 9b | 9b |  | 0
180 | Satna | 2 | 315 | 400/220 | PGCIL | 9b | 9b |  | 1
181 | Satpura | 1 | 500 | 400/220 | MPPTCL | 9 | 10 |  | 0
182 | Seoni | 1 | 315 | 400/220 | PGCIL | 9b | 9 | MP | 0
183 | Seoni | 2 | 315 | 400/220 | PGCIL | 9b | 9 |  | 1
184 | Sholapur-M | 1 | 500 | 400/220 | MSETCL | 9 | 11 |  | 0
185 | Sholapur-M | 2 | 500 | 400/220 | MSETCL | 9 | 11 |  | 1
186 | Shujalpur | 1 | 315 | 400/220 | PGCIL | 9b | 9b |  | 0
187 | Shujalpur | 2 | 315 | 400/220 | PGCIL | 9b | 9b |  | 1
188 | Soja | 1 | 500 | 400/220 | GETCO | 9 | 11 |  | 0
189 | Soja | 2 | 500 | 400/220 | GETCO | 9 | 11 |  | 1
190 | Solapur-PG | 3 | 500 | 400/220 | PGCIL | 9 | 9 |  | 0
191 | Solapur-PG | 1 | 315 | 400/220 | PGCIL | 9b | 9 |  | 1
192 | Solapur-PG | 2 | 315 | 400/220 | PGCIL | 9b | 9 |  | 1
193 | SSP | 1 | 315 | 400/220 | SSNL | 9b | 9b |  | 0
194 | SSP | 2 | 315 | 400/220 | SSNL | 9b | 9b |  | 1
195 | Sugen | 1 | 315 | 400/220 | TPL | 9b | 1 |  | 0
196 | Sugen | 2 | 315 | 400/220 | TPL | 9b | 1 |  | 1
197 | Sugen | 3 | 315 | 400/220 | TPL | 9b | 1 |  | 1
198 | Ukai | 1 | 315 | 400/220 | GETCO | 9b | 9 |  | 0
199 | Vapi | 1 | 315 | 400/220 | PGCIL | 9b | 12 |  | 0
200 | Vapi | 2 | 315 | 400/220 | PGCIL | 9b | 12 |  | 1
201 | Vapi | 3 | 315 | 400/220 | PGCIL | 9b | 12 |  | 1
202 | Varsana | 1 | 315 | 400/220 | GETCO | 9b | 5 |  | 0
203 | Varsana | 2 | 315 | 400/220 | GETCO | 9b | 5 |  | 1
204 | Wanakbori | 1 | 315 | 400/220 | GETCO | 9b | 9 |  | 0
205 | Wardha | 3 | 500 | 400/220 | PGCIL | 9 | 9b |  | 0
206 | Wardha | 1 | 315 | 400/220 | PGCIL | 9b | 9b |  | 1
207 | Wardha | 2 | 315 | 400/220 | PGCIL | 9b | 9b |  | 1
208 | Warora | 1 | 500 | 400/220 | MEGPTCL | 9 | 9 |  | 0
209 | Warora | 2 | 500 | 400/220 | MEGPTCL | 9 | 9 |  | 1
210 | Zerda(Kansari) | 1 | 315 | 400/220 | PGCIL | 9b | 11 |  | 0
211 | Zerda(Kansari) | 2 | 315 | 400/220 | PGCIL | 9b | 11 |  | 1
212 | Zerda(Kansari) | 3 | 315 | 400/220 | PGCIL | 9b | 11 |  | 1
|  | Total | 75330

## 765 SC MVA
Sl. Nos | BUS | kV | Three Phase Fault
|  |  | Three phase fault current (kA) | Three phase fault MVA
1 | Akola(2) | 765 | 9.169 | 12148.7416
2 | Aurangabad-PG | 765 | 24.1471 | 31994.4246
3 | Bhopal-BDTCL | 765 | 16.3958 | 21724.1071
4 | Bilaspur | 765 | 30.3367 | 40195.5208
5 | Bina-PG | 765 | 35.3771 | 46873.95
6 | Champa | 765 | 14.7255 | 19510.993
7 | Dharamjaygarh | 765 | 30.3062 | 40155.1089
8 | Dhule-BDTCL | 765 | 10.656 | 14118.9869
9 | Gwalior | 765 | 33.1638 | 43941.3717
10 | Indore-PG | 765 | 17.6409 | 23373.8397
11 | Jabalpur-PS | 765 | 27.6501 | 36635.8295
12 | Koradi(III) | 765 | 9.146 | 12118.2671
13 | Pune-PG(Shikrapur) | 765 | 9.0036 | 11929.5899
14 | Raigarh-PS(Kotra) | 765 | 23.0255 | 30508.327
15 | Raipur-PS(Durg) | 765 | 24.4016 | 32331.632
16 | Sasan | 765 | 33.3174 | 44144.8887
17 | Satna | 765 | 30.741 | 40731.2102
18 | Seoni | 765 | 24.6469 | 32656.6496
19 | Sipat | 765 | 21.2259 | 28123.893
20 | Solapur | 765 | 29.4363 | 39002.5088
21 | Tamnar | 765 | 20.0462 | 26560.8141
22 | Tiroda | 765 | 10.0606 | 13330.0938
23 | Vadodora-PS | 765 | 14.8686 | 19700.5976
24 | Vindhyachal-PS | 765 | 31.6647 | 41955.0942
25 | Wardha | 765 | 30.0332 | 39793.3893

## DD DNH ICTS
Sl No | Sub-Station | Ckt ID | MVA | Voltage Ratio | Owner | Normal Tap Position | Present Tap Position
1 | Khadoli | 1 | 160 | 220/66 | Electricity Dep of DNH | 9 | 9
2 | Khadoli | 2 | 160 | 220/66 | Electricity Dep of DNH | 9 | 9
3 | Kharadpada | 1 | 100 | 220/66 | Electricity Dep of DNH | 9 | 9
4 | Kharadpada | 2 | 100 | 220/66 | Electricity Dep of DNH | 9 | 9
5 | Kharadpada | 3 | 100 | 220/66 | Electricity Dep of DNH | 9 | 9
6 | Kharadpada | 4 | 100 | 220/66 | Electricity Dep of DNH | 9 | 9
7 | Magarwara | 1 | 50 | 220/66 | Electricity Dep of DD | 9 | 9
8 | Magarwara | 2 | 100 | 220/66 | Electricity Dep of DD | 9 | 9
9 | Magarwara | 3 | 100 | 220/66 | Electricity Dep of DD | 9 | 9
10 | Magarwara | 4 | 160 | 220/66 | Electricity Dep of DD | 9 | 9

## 220kV Lines
Sl No | End-1 | End-2 | Id | Line Owner | End-1 Owner | End-2 Owner | Length(in Km) | Conductor Type
1 | Anuppur | Kotmikala | 1 | MPPTCL | CSPTCL | MPPTCL | 61 | Single Zebra
2 | Anuppur | Kotmikala | 2 | MPPTCL | CSPTCL | MPPTCL | 61 | Single Zebra
3 | Auraiya | Malanpur | 1 | MPPTCL | UPPTCL | MPPTCL | 146 | Single Zebra
4 | Auraiya | Mehgaon | 1 | MPPTCL | UPPTCL | MPPTCL | 113 | Single Zebra
5 | Aurangabad-PG | Chitegoan | 1 | MSETCL | WRTS-1 | MSETCL | 34 | Single Zebra
6 | Aurangabad-PG | Chitegoan | 2 | MSETCL | WRTS-1 | MSETCL | 34 | Single Zebra
7 | Aurangabad-PG | Shendra | 1 | MSETCL | WRTS-1 | MSETCL | 11 | Single Zebra
8 | Aurangabad-PG | Shendra | 2 | MSETCL | WRTS-1 | MSETCL | 11 | Single Zebra
9 | Badod | Sakatpur | 1 | MPPTCL | MPPTCL | RSPTCL | 199 | Single Zebra
10 | Badod | Nepniya | 1 | MPPTCL | MPPTCL | RSPTCL | 62 | Single Zebra
11 | Bhanpura | Modak | 1 | MPPTCL | MPPTCL | MPPTCL | 63 | Single Zebra
12 | Bhatapara-PG | Bhatapara-CG | 1 | CSPTCL | WRTS-1 | CSPTCL | 7 | Single Zebra
13 | Bhatapara-PG | Suhela | 1 | CSPTCL | WRTS-1 | CSPTCL | 19 | Single Zebra
14 | Bhatapara-PG | Suhela | 2 | CSPTCL | WRTS-1 | CSPTCL | 19 | Single Zebra
15 | Bhatapara-PG | Suhela | 3 | CSPTCL | WRTS-1 | CSPTCL | 19 | Single Zebra
16 | Bhilad | Vapi-PG | 1 | GETCO | GETCO | WRTS-2 | 21 | Single Zebra
17 | Bhilad | Vapi-PG | 2 | GETCO | GETCO | WRTS-2 | 22 | Single Zebra
18 | Bhilad | Vapi-PG | 3 | GETCO | GETCO | WRTS-2 | 22 | Single Zebra
19 | Bina-MP | Bina-PG | 1 | MPPTCL | MPPTCL | WRTS-2 | 3 | Single Zebra
20 | Bina-MP | Shivpuri | 1 | MPPTCL | MPPTCL | MPPTCL | 169 | Single Zebra
21 | Bina-MP | Mahalgaon | 1 | MPPTCL | MPPTCL | MPPTCL | 246 | Single Zebra
22 | Bina-MP | Mahalgaon | 2 | MPPTCL | MPPTCL | MPPTCL | 246 | Single Zebra
23 | Boisar-PG | Vasai | 1 | MSETCL | WRTS-1 | MSETCL | 11 | Single Zebra
24 | Boisar-PG | Boisar-M | 1 | MSETCL | WRTS-1 | MSETCL | 53 | Single Zebra
25 | Boisar-PG | Boisar-M | 2 | MSETCL | WRTS-1 | MSETCL | 53 | Single Zebra
26 | Damoh-MP | Damoh-PG | 1 | MPPTCL | MPPTCL | WRTS-2 | 8 | Single Zebra
27 | Damoh-MP | Damoh-PG | 2 | MPPTCL | MPPTCL | WRTS-2 | 9 | Single Zebra
28 | Damoh-PG | Sagar | 2 | MPPTCL | WRTS-2 | MPPTCL | 62 | Single Zebra
29 | Damoh-PG | Tikamgad | 1 | MPPTCL | WRTS-2 | MPPTCL | 151 | Single Zebra
30 | Dehgam | Ranasan | 1 | GETCO | WRTS-2 | GETCO | 20 | Single Zebra
31 | Dehgam | Ranasan | 2 | GETCO | WRTS-2 | GETCO | 20 | Single Zebra
32 | Dehgam | Khanpur | 1 | GETCO | WRTS-2 | GETCO | 12 | Single Zebra
33 | Dehgam | Khanpur | 2 | GETCO | WRTS-2 | GETCO | 12 | Single Zebra
34 | Gandhar | Haldarwa | 2 | GETCO | NTPC | GETCO | 13 | Single Zebra
35 | Gandhar | Haldarwa | 1 | GETCO | NTPC | GETCO | 13 | Single Zebra
36 | Gwalior | Malanpur | 1 | MPPTCL | WRTS-2 | MPPTCL | 38 | Single Zebra
37 | Gwalior | Malanpur | 2 | MPPTCL | WRTS-2 | MPPTCL | 38 | Single Zebra
38 | Gwalior | Mahalgaon | 1 | MPPTCL | WRTS-2 | MPPTCL | 11 | Single Zebra
39 | Gwalior | Mahalgaon | 2 | MPPTCL | WRTS-2 | MPPTCL | 11 | Single Zebra
40 | Gwalior | Gwalior-II | 1 | MPPTCL | WRTS-3 | MPPTCL | 3 | Single Zebra
41 | Gwalior | Gwalior-II | 2 | MPPTCL | WRTS-4 | MPPTCL | 3 | Single Zebra
42 | Halkarni | Tillari | 1 | MSETCL | MSETCL | MSETCL | 29 | Single Zebra
43 | Halvad | Bhimasar | 1 | GETCO | GETCO | GETCO | 150 | Single Zebra
44 | Halvad | Bhimasar | 2 | GETCO | GETCO | GETCO | 150 | Single Zebra
45 | Hoshangabad | Itarsi-PG | 1 | MPPTCL | MPPTCL | WRTS-2 | 21 | Single Zebra
46 | Itarsi | Itarsi-PG | 1 | MPPTCL | MPPTCL | WRTS-2 | 3 | Single Zebra
47 | Jabalpur | Jabalpur-PG | 1 | MPPTCL | MPPTCL | WRTS-2 | 11 | Single Zebra
48 | Jabalpur | Jabalpur-PG | 2 | MPPTCL | MPPTCL | WRTS-2 | 11 | Single Zebra
49 | Kakrapar | Haldarwa | 1 | GETCO | NPCIL | GETCO | 74 | Single Zebra
50 | Kakrapar | Haldarwa | 2 | GETCO | NPCIL | GETCO | 74 | Single Zebra
51 | Kakrapar | Vav | 1 | GETCO | NPCIL | GETCO | 43 | Single Zebra
52 | Kakrapar | Vav | 2 | GETCO | NPCIL | GETCO | 43 | Single Zebra
53 | Kakrapar | Vapi-PG | 1 | NPCIL | NPCIL | WRTS-2 | 117 | Single Zebra
54 | Kakrapar | Vapi-PG | 2 | NPCIL | NPCIL | WRTS-2 | 117 | Single Zebra
55 | Kala | Kharadpada-PG | 1 | DNH | WRTS-2 | DNH | 30 | Single Zebra
56 | Kala | Kharadpada-PG | 2 | DNH | WRTS-2 | DNH | 30 | Single Zebra
57 | Kala | Khadoli | 1 | DNH |  |  | 8 | Single Zebra
58 | Kala | Khadoli | 2 | DNH |  |  | 8 | Single Zebra
59 | Katni | Satna-PG | 1 | MPPTCL | MPPTCL | WRTS-2 | 102 | Single Zebra
60 | Kawas | Haldarwa | 1 | WRTS-2 | NTPC | GETCO | 81 | Single Zebra
61 | Kawas | Haldarwa | 2 | WRTS-2 | NTPC | GETCO | 81 | Single Zebra
62 | Kawas | Navsari-PG | 1 | WRTS-2 | NTPC | WRTS-2 | 56 | Single Zebra
63 | Kawas | Navsari-PG | 2 | WRTS-2 | NTPC | WRTS-2 | 56 | Single Zebra
64 | Kawas | Vav | 1 | GETCO | NTPC | GETCO | 37 | Single Zebra
65 | Kawas | Vav | 2 | GETCO | NTPC | GETCO | 37 | Single Zebra
66 | Kawas | Ichchapur | 1 | GETCO | NTPC | GETCO | 3 | Single Zebra
67 | Kawas | Ichchapur | 2 | GETCO | NTPC | GETCO | 3 | Single Zebra
68 | Khandwa | Omkareswar | 1 | MPPTCL | WRTS-2 | MPPTCL | 98 | Single Zebra
69 | Kharadpada-PG | Kharadpada-DNH | 1 | DNH |  |  | 1 | Single Zebra
70 | Kharadpada-PG | Kharadpada-DNH | 2 | DNH |  |  | 1 | Single Zebra
71 | Kolhapur | Mumbewadi | 1 | MSETCL | MSETCL | MSETCL | 52 | Single Zebra
72 | Kolhapur(Mudshingi) | Chikkodi | 1 | KPTCL/MSETCL | MSETCL | KPTCL | 155 | Single Zebra
73 | Kolhapur(Talandage) | Kolhapur(Mudshingi) | 1 | MSETCL | MSETCL | MSETCL | 5 | Single Zebra
74 | Kolhapur(Talandage) | Kolhapur(Mudshingi) | 2 | MSETCL | MSETCL | MSETCL | 5 | Single Zebra
75 | Kolhapur(Talandage) | Chikkodi | 1 | KPTCL/MSETCL | MSETCL | KPTCL | 150 | Single Zebra
76 | Konalkatta | Amona | 1 | MSETCL | MSETCL | GED | 28 | Single Zebra
77 | Korba East | Budhipadar | 2 | OPTCL | CSPTCL | OPTCL | 176 | Single Zebra
78 | Korba East | Budhipadar | 3 | OPTCL | CSPTCL | OPTCL | 176 | Single Zebra
79 | Korba East | Raigarh | 1 | WRTS-1 | CSPTCL | CSPTCL | 110 | Single Zebra
80 | Magarwada-PG | Magarwada-DD | 1 | DD | WRTS-2 | DD | 2 | Single Zebra
81 | Magarwada-PG | Magarwada-DD | 2 | DD | WRTS-2 | DD | 2 | Single Zebra
82 | Mapusa | Amona | 1 | WRTS-1 | WRTS-1 | GED | 25 | Single Zebra
83 | Mapusa | Ponda | 1 | WRTS-1 | WRTS-1 | GED | 43 | Single Zebra
84 | Mapusa | Tivim | 1 | WRTS-1 | WRTS-1 | GED | 5 | Single Zebra
85 | Mapusa | Tivim | 2 | WRTS-1 | WRTS-1 | GED | 5 | Single Zebra
86 | Mehgaon | Malanpur | 1 | MPPTCL | MPPTCL | MPPTCL | 37 | Single Zebra
87 | Morbi | Hadala | 2 | GETCO | GETCO | GETCO | 59 | Single Zebra
88 | Morbi | Halvad | 1 | GETCO | GETCO | GETCO | 43 | Single Zebra
89 | Mumewadi | Halkarni | 1 | MSETCL | MSETCL | MSETCL | 49 | Single Zebra
90 | Nasik | Navsari | 1 | MSETCL | MSETCL | GETCO | 171 | Single Zebra
91 | Nasik | Navsari | 2 | MSETCL | MSETCL | GETCO | 171 | Single Zebra
92 | Navsari-PG | Navsari | 1 | WRTS-2 | WRTS-2 | WRTS-2 | 10 | Single Zebra
93 | Navsari-PG | Navsari | 2 | GETCO | WRTS-2 | GETCO | 10 | Single Zebra
94 | Nepniya | Bhanpura | 1 | MPPTCL | MPPTCL | MPPTCL | 51 | Single Zebra
95 | Pandurna | Kalmeshwar | 1 | MSETCL/MPPTCL | MPPTCL | MSETCL | 68 | Single Zebra
96 | Pithampura | Rajgarh-PG | 1 | MPPTCL | MPPTCL | WRTS-1 | 79 | Single Zebra
97 | Pithampura | Rajgarh-PG | 2 | MPPTCL | MPPTCL | WRTS-1 | 78 | Single Zebra
98 | Ponda | Ambewadi | 1 | GED/KPTCL | GED | KPTCL | 120 | Single Zebra
99 | Raigarh-CG | Bhudhipadar | 1 | WRTS-1 | CSPTCL | OPTCL | 105 | Single Zebra
100 | Raigarh-PG | Raigarh-CG | 1 | CSPTCL | WRTS-1 | CSPTCL | 15 | Single Zebra
101 | Raigarh-PG | Raigarh-CG | 2 | CSPTCL | WRTS-1 | CSPTCL | 15 | Single Zebra
102 | Rajgarh-PG | Rajgarh-MP | 1 | MPPTCL | WRTS-2 | MPPTCL | 13 | Single Zebra
103 | Rajgarh-PG | Dhar | 1 | MPPTCL | WRTS-2 | MPPTCL | 12 | Single Zebra
104 | Satna-MP | Satna-PG | 1 | MPPTCL | MPPTCL | WRTS-2 | 1 | Single Zebra
105 | Satna-MP | Satna-PG | 2 | MPPTCL | MPPTCL | WRTS-2 | 1 | Single Zebra
106 | Satna-PG | Maihar | 2 | MPPTCL | WRTS-2 | MPPTCL | 42 | Single Zebra
107 | Seoni-PG | Seoni-MP | 1 | MPPTCL | WRTS-1 | MPPTCL | 4 | Single Zebra
108 | Seoni-PG | Seoni-MP | 2 | MPPTCL | WRTS-1 | MPPTCL | 4 | Single Zebra
109 | Seoni-PG | Chindwara | 1 | MPPTCL | WRTS-1 | MPPTCL | 67 | Single Zebra
110 | Seoni-PG | Chindwara | 2 | MPPTCL | WRTS-1 | MPPTCL | 67 | Single Zebra
111 | Sholapur-PG | Kumbari | 1 | WRTS-1 | WRTS-1 | MSETCL | 7 | Single Zebra
112 | Sholapur-PG | Kumbari | 2 | WRTS-1 | WRTS-1 | MSETCL | 7 | Single Zebra
113 | Shujalpur | Shujalpur-MP | 1 | MPPTCL |  |  | 4 | Single Zebra
114 | Shujalpur | Shujalpur-MP | 2 | MPPTCL |  |  | 4 | Single Zebra
115 | Talegaon | Pune-PG | 1 | MSETCL | MSETCL | WRTS-1 | 4 | Single Zebra
116 | Talegaon | Pune-PG | 2 | MSETCL | MSETCL | WRTS-1 | 4 | Single Zebra
117 | Tarapur-1&2 | Vapi | 1 | WRTS-1 | NPCIL | GETCO | 117 | Single Zebra
118 | Tarapur-1&2 | Bhilad | 1 | WRTS-1 | NPCIL | GETCO | 62 | Single Zebra
119 | Tarapur-1&2 | Boisar-M | 1 | WRTS-1 | NPCIL | MSETCL | 20 | Single Zebra
120 | Tarapur-1&2 | Borivali | 1 | WRTS-1 | NPCIL | MSETCL | 96 | Single Zebra
121 | Tarapur-3&4 | Boisar-PG | 1 | WRTS-1 | NPCIL | MSETCL | 21 | Single Zebra
122 | Tarapur-3&4 | Tarapur-1&2 | 1 | WRTS-1 | NPCIL | NPCIL | 1 | Single Zebra
123 | Tillari | Amona | 1 | MSETCL | MSETCL | GED | 37 | Single Zebra
124 | Vapi-PG | Magarwada | 1 | WRTS-2 | WRTS-2 | DD | 26 | Single Zebra
125 | Vapi-PG | Magarwada | 2 | WRTS-2 | WRTS-2 | DD | 26 | Single Zebra
126 | Vapi-PG | Kharadpada-DNH | 1 | WRTS-2 | WRTS-2 | DNH | 30 | Single Zebra
127 | Vapi-PG | Kharadpada-DNH | 2 | WRTS-2 | WRTS-2 | DNH | 30 | Single Zebra
128 | Vapi-PG | Khadoli | 1 | WRTS-2 | WRTS-2 | DNH | 28 | Single Zebra
129 | Vapi-PG | Sayali | 1 | WRTS-2 | WRTS-2 | DNH | 19 | Single Zebra
130 | Wardha-PG | Wardha-M | 1 | MSETCL | WRTS-1 | MSETCL | 25 | Single Zebra
131 | Wardha-PG | Badnera | 1 | MSETCL | WRTS-1 | MSETCL | 95 | Single Zebra
132 | Xeldem | Ambewadi | 1 | GED/KPTCL | GED | KPTCL | 120 | Single Zebra
|  |  |  | Total |  | Sub-Total | 6618

## RGMO FGMO_States
List of Generators Mandated for RGMO/FGMO by IEGC
Maharashtra
Sl. No. | Name of Station | Name of Stage/ Unit | Installed capacity (MW) | Name of Utility | Sector (CS/SS/Private)
1 | APL-Tiroda | 1 | 660 | Adani Power | Private
2 | APL-Tiroda | 2 | 660 | Adani Power | Private
3 | APL-Tiroda | 3 | 660 | Adani Power | Private
4 | APL-Tiroda | 4 | 660 | Adani Power | Private
5 | APL-Tiroda | 5 | 660 | Adani Power | Private
6 | Bhadardhara (Hy) | 1 | 23 | Tata Hydro | Private
7 | Bhadardhara (Hy) | 2 | 23 | Tata Hydro | Private
8 | Bhatghar | 1 | 16 | Tata Hydro | Private
9 | Bhatsa (Hy) | 1 | 15 | Tata Hydro | Private
10 | Bhira (Hy) | 1 | 25 | Tata Hydro | Private
11 | Bhira (Hy) | 2 | 25 | Tata Hydro | Private
12 | Bhira (Hy) | 3 | 25 | Tata Hydro | Private
13 | Bhira (Hy) | 4 | 25 | Tata Hydro | Private
14 | Bhira (Hy) | 5 | 25 | Tata Hydro | Private
15 | Bhira (Hy) | 6 | 25 | Tata Hydro | Private
16 | Bhira PSS (Hy) | 1 | 150 | Tata Hydro | Private
17 | Bhira Tailrace (Hy) | 1 | 40 | Tata Hydro | Private
18 | Bhira Tailrace (Hy) | 2 | 40 | Tata Hydro | Private
19 | Bhivpuri (Hy) | 4 | 12 | Tata Hydro | Private
20 | Bhivpuri (Hy) | 5 | 12 | Tata Hydro | Private
21 | Bhivpuri (Hy) | 1 | 24 | Tata Hydro | Private
22 | Bhivpuri (Hy) | 2 | 24 | Tata Hydro | Private
23 | Bhivpuri (Hy) | 3 | 24 | Tata Hydro | Private
24 | Bhusawal | 2 | 210 | MahaGenco | SS
25 | Bhusawal | 3 | 210 | MahaGenco | SS
26 | Bhusawal | 4 | 500 | MahaGenco | SS
27 | Bhusawal | 5 | 500 | MahaGenco | SS
28 | Chadrapur | 1 | 210 | MahaGenco | SS
29 | Chadrapur | 2 | 210 | MahaGenco | SS
30 | Chadrapur | 3 | 210 | MahaGenco | SS
31 | Chadrapur | 4 | 210 | MahaGenco | SS
32 | Chadrapur | 5 | 500 | MahaGenco | SS
33 | Chadrapur | 6 | 500 | MahaGenco | SS
34 | Chadrapur | 7 | 500 | MahaGenco | SS
35 | Chadrapur Ext | 1 | 500 | MahaGenco | SS
36 | Dhahanu | 1 | 250 | Reliance Energy | Private
37 | Dhahanu | 2 | 250 | Reliance Energy | Private
38 | Dhariwal | 1 | 300 | Dhariwal Infrastructure | Private
39 | Dudhganga (Hy) | 1 | 12 | Tata Hydro | Private
40 | Dudhganga (Hy) | 2 | 12 | Tata Hydro | Private
41 | Ghatghar (Hy) | 1 | 125 | Tata Hydro | Private
42 | Ghatghar (Hy) | 2 | 125 | Tata Hydro | Private
43 | IEPL | 1 | 270 | IEPL | Private
44 | Nandgaonpeth | 1 | 270 | Rattan India | Private
45 | Nandgaonpeth | 2 | 270 | Rattan India | Private
46 | Nandgaonpeth | 3 | 270 | Rattan India | Private
47 | Nandgaonpeth | 4 | 270 | Rattan India | Private
48 | Nandgaonpeth | 5 | 270 | Rattan India | Private
49 | JSW Ratnagiri | 1 | 300 | JSW | Private
50 | JSW Ratnagiri | 2 | 300 | JSW | Private
51 | JSW Ratnagiri | 3 | 300 | JSW | Private
52 | JSW Ratnagiri | 4 | 300 | JSW | Private
53 | Khaparkheda | 1 | 210 | MahaGenco | SS
54 | Khaparkheda | 2 | 210 | MahaGenco | SS
55 | Khaparkheda | 3 | 210 | MahaGenco | SS
56 | Khaparkheda | 4 | 210 | MahaGenco | SS
57 | Khaparkheda | 5 | 500 | MahaGenco | SS
58 | Koradi | 5 | 200 | MahaGenco | SS
59 | Koradi | 6 | 210 | MahaGenco | SS
60 | Koradi | 7 | 210 | MahaGenco | SS
61 | Koradi-II | 8 | 660 | MahaGenco | SS
62 | Koradi-II | 9 | 660 | MahaGenco | SS
63 | Koyna DPH (Hy) | 1 | 20 | MahaGenco | SS
64 | Koyna DPH (Hy) | 2 | 20 | MahaGenco | SS
65 | Koyna-I & II (Hy) | 1 | 70 | MahaGenco | SS
66 | Koyna-I & II (Hy) | 2 | 70 | MahaGenco | SS
67 | Koyna-I & II (Hy) | 3 | 70 | MahaGenco | SS
68 | Koyna-I & II (Hy) | 4 | 70 | MahaGenco | SS
69 | Koyna-I & II (Hy) | 5 | 80 | MahaGenco | SS
70 | Koyna-I & II (Hy) | 6 | 80 | MahaGenco | SS
71 | Koyna-I & II (Hy) | 7 | 80 | MahaGenco | SS
72 | Koyna-I & II (Hy) | 8 | 80 | MahaGenco | SS
73 | Koyna-III (Hy) | 9 | 80 | MahaGenco | SS
74 | Koyna-III (Hy) | 10 | 80 | MahaGenco | SS
75 | Koyna-III (Hy) | 11 | 80 | MahaGenco | SS
76 | Koyna-III (Hy) | 12 | 80 | MahaGenco | SS
77 | Koyna-IV (Hy) | 1 | 250 | MahaGenco | SS
78 | Koyna-IV (Hy) | 2 | 250 | MahaGenco | SS
79 | Koyna-IV (Hy) | 3 | 250 | MahaGenco | SS
80 | Koyna-IV (Hy) | 4 | 250 | MahaGenco | SS
81 | Nasik | 3 | 210 | MahaGenco | SS
82 | Nasik | 4 | 210 | MahaGenco | SS
83 | Nasik | 5 | 210 | MahaGenco | SS
84 | Nasik-Rattan India | 1 | 270 | Rattan India | Private
85 | Paithan (Hy) | 1 | 12 | MahaGenco | SS
86 | Paras | 3 | 250 | MahaGenco | SS
87 | Paras | 4 | 250 | MahaGenco | SS
88 | Parli | 3 | 210 | MahaGenco | SS
89 | Parli | 4 | 210 | MahaGenco | SS
90 | Parli | 5 | 210 | MahaGenco | SS
91 | Parli | 6 | 250 | MahaGenco | SS
92 | Parli | 7 | 250 | MahaGenco | SS
93 | Pawana (Hy) | 1 | 10 | Tata Hydro | Private
94 | Tillari (Hy) | 1 | 60 | MahaGenco | SS
95 | Trombay | 8 | 250 | MahaGenco | SS
96 | Trombay | 5 | 500 | MahaGenco | SS
97 | Trombay | 6 | 500 | MahaGenco | SS
98 | Ujjani (Hy) | 1 | 12 | MahaGenco | SS
99 | Vaitharna (Hy) | 1 | 60 | MahaGenco | SS
100 | Vidarbha Industry | 1 | 300 | VIPCL | Private
101 | Vidarbha Industry | 2 | 300 | VIPCL | Private
|  | Total | 21781 |  |  | 290
Gujarat
Sl. No. | Name of Station | Name of Stage/ Unit | Installed capacity (MW) | Name of Utility | Sector (CS/SS/Private)
1 | APL_Mundra | 1 | 330 | APL | Private
2 | APL_Mundra | 2 | 330 | APL | Private
3 | APL_Mundra | 3 | 330 | APL | Private
4 | APL_Mundra | 4 | 330 | APL | Private
5 | APL_Mundra | 5 | 660 | APL | Private
6 | APL_Mundra | 6 | 660 | APL | Private
7 | APL_Mundra | 7 | 660 | APL | Private
8 | APL_Mundra | 8 | 660 | APL | Private
9 | APL_Mundra | 9 | 660 | APL | Private
10 | Dhuvaran | 3 | 376 | GSECL | SS
11 | Gandhinagar | 3 | 210 | GSECL | SS
12 | Gandhinagar | 4 | 210 | GSECL | SS
13 | Gandhinagar | 5 | 210 | GSECL | SS
14 | Kadana (Hy) | 1 | 60 | GSECL | SS
15 | Kadana (Hy) | 2 | 60 | GSECL | SS
16 | Kadana (Hy) | 3 | 60 | GSECL | SS
17 | Kadana (Hy) | 4 | 60 | GSECL | SS
18 | Sikka | 4 | 250 | GSECL | SS
19 | Ukai (Hy) | 1 | 75 | GSECL | SS
20 | Ukai (Hy) | 2 | 75 | GSECL | SS
21 | Ukai (Hy) | 3 | 75 | GSECL | SS
22 | Ukai (Hy) | 4 | 75 | GSECL | SS
23 | Ukai (Th) | 3 | 200 | GSECL | SS
24 | Ukai (Th) | 4 | 200 | GSECL | SS
25 | Ukai (Th) | 5 | 210 | GSECL | SS
26 | Ukai (Th) | 6 | 500 | GSECL | SS
27 | Vadinar | 1 | 600 | Vadinar Power Company | Private
28 | Vadinar | 2 | 600 | Vadinar Power Company | Private
29 | Wanakbori | 1 | 210 | GSECL | SS
30 | Wanakbori | 2 | 210 | GSECL | SS
31 | Wanakbori | 3 | 210 | GSECL | SS
32 | Wanakbori | 4 | 210 | GSECL | SS
33 | Wanakbori | 5 | 210 | GSECL | SS
34 | Wanakbori | 6 | 210 | GSECL | SS
35 | Wanakbori | 7 | 210 | GSECL | SS
|  | Total | 10196
Madhya Pradesh
Sl. No. | Name of Station | Name of Stage/ Unit | Installed capacity (MW) | Name of Utility | Sector (CS/SS/Private)
1 | Amarkantak | 5 | 210 | MPGCL | SS
2 | Bansagar Tons (Hy) | 1 | 105 | MPGCL | SS
3 | Bansagar Tons (Hy) | 2 | 105 | MPGCL | SS
4 | Bansagar Tons (Hy) | 3 | 105 | MPGCL | SS
5 | Bansagar-Deolon(Hy) | 1 | 20 | MPGCL | SS
6 | Bansagar-Deolon(Hy) | 3 | 20 | MPGCL | SS
7 | Bansagar-Deolon(Hy) | 2 | 20 | MPGCL | SS
8 | Bansagar-Jhinna(Hy) | 1 | 10 | MPGCL | SS
9 | Bansagar-Jhinna(Hy) | 2 | 10 | MPGCL | SS
10 | Bansagar-Silpara(Hy) | 1 | 15 | MPGCL | SS
11 | Bansagar-Silpara(Hy) | 2 | 15 | MPGCL | SS
12 | Bargi (Hy) | 1 | 50 | MPGCL | SS
13 | Bargi (Hy) | 2 | 50 | MPGCL | SS
14 | Birsinghpur (Hy) | 1 | 20 | MPGCL | SS
15 | Gandhisagar | 1 | 23 | MPGCL | SS
16 | Gandhisagar | 2 | 23 | MPGCL | SS
17 | Gandhisagar | 3 | 23 | MPGCL | SS
18 | Gandhisagar | 4 | 23 | MPGCL | SS
19 | Gandhisagar | 5 | 23 | MPGCL | SS
20 | Indirasagar (Hy) | 1 | 125 | MPGCL | SS
21 | Indirasagar (Hy) | 2 | 125 | MPGCL | SS
22 | Indirasagar (Hy) | 3 | 125 | MPGCL | SS
23 | Indirasagar (Hy) | 4 | 125 | MPGCL | SS
24 | Indirasagar (Hy) | 5 | 125 | MPGCL | SS
25 | Indirasagar (Hy) | 6 | 125 | MPGCL | SS
26 | Indirasagar (Hy) | 7 | 125 | MPGCL | SS
27 | Indirasagar (Hy) | 8 | 125 | MPGCL | SS
28 | JP Bina | 1 | 250 | Jaypee Group | Private
29 | JP Bina | 2 | 250 | Jaypee Group | Private
30 | Madhikheda (Hy) | 1 | 20 | MPGCL | SS
31 | Madhikheda (Hy) | 2 | 20 | MPGCL | SS
32 | Madhikheda (Hy) | 3 | 20 | MPGCL | SS
33 | Omkareshwar (Hy) | 1 | 65 | MPGCL | SS
34 | Omkareshwar (Hy) | 2 | 65 | MPGCL | SS
35 | Omkareshwar (Hy) | 3 | 65 | MPGCL | SS
36 | Omkareshwar (Hy) | 4 | 65 | MPGCL | SS
37 | Omkareshwar (Hy) | 5 | 65 | MPGCL | SS
38 | Omkareshwar (Hy) | 6 | 65 | MPGCL | SS
39 | Omkareshwar (Hy) | 7 | 65 | MPGCL | SS
40 | Omkareshwar (Hy) | 8 | 65 | MPGCL | SS
41 | Pench (Hy) | 1 | 80 | MPGCL | SS
42 | Pench (Hy) | 2 | 80 | MPGCL | SS
43 | Rajghat(Hy) | 1 | 15 | MPGCL | SS
44 | Rajghat(Hy) | 2 | 15 | MPGCL | SS
45 | Rajghat(Hy) | 3 | 15 | MPGCL | SS
46 | Sanjay Gandhi TPS | 1 | 210 | MPGCL | SS
47 | Sanjay Gandhi TPS | 2 | 210 | MPGCL | SS
48 | Sanjay Gandhi TPS | 3 | 210 | MPGCL | SS
49 | Sanjay Gandhi TPS | 4 | 210 | MPGCL | SS
50 | Sanjay Gandhi TPS-II | 5 | 500 | MPGCL | SS
51 | Satpura-II | 6 | 200 | MPGCL | SS
52 | Satpura-II | 7 | 210 | MPGCL | SS
53 | Satpura-III | 8 | 210 | MPGCL | SS
54 | Satpura-III | 9 | 210 | MPGCL | SS
55 | Satpura-IV | 10 | 250 | MPGCL | SS
56 | Satpura-IV | 11 | 250 | MPGCL | SS
57 | Singhaji | 1 | 600 | MPGCL | SS
58 | Singhaji | 2 | 600 | MPGCL | SS
|  | Total | 7025
Chhattisgarh
Sl. No. | Name of Station | Name of Stage/ Unit | Installed capacity (MW) | Name of Utility | Sector (CS/SS/Private)
1 | Hasdeo Bango (Hy) | 1 | 40 | CSPGCL | SS
2 | Hasdeo Bango (Hy) | 2 | 40 | CSPGCL | SS
3 | Hasdeo Bango (Hy) | 3 | 40 | CSPGCL | SS
4 | Korba (E) extn | 1 | 250 | CSPGCL | SS
5 | Korba (E) extn | 2 | 250 | CSPGCL | SS
6 | Korba (W) | 1 | 210 | CSPGCL | SS
7 | Korba (W) | 2 | 210 | CSPGCL | SS
8 | Korba (W) | 3 | 210 | CSPGCL | SS
9 | Korba (W) | 4 | 210 | CSPGCL | SS |  | 200
10 | Korba (W) | 5 | 500 | CSPGCL | SS
11 | Marwa | 1 | 500 | CSPGCL | SS
|  | Sub total | 2460

## RGMO FGMO_CS
Central Sector
Sl. No. | Name of Station | Name of Stage/ Unit | Installed capacity (MW) | Name of Utility | Sector (CS/SS/Private)
1 | Korba STPS | 1 | 200 | NTPC Ltd | CS
2 | Korba STPS | 2 | 200 | NTPC Ltd | CS
3 | Korba STPS | 3 | 200 | NTPC Ltd | CS
4 | Korba STPS | 4 | 500 | NTPC Ltd | CS
5 | Korba STPS | 5 | 500 | NTPC Ltd | CS
6 | Korba STPS | 6 | 500 | NTPC Ltd | CS
7 | Korba STPS | 7 | 500 | NTPC Ltd | CS
8 | Mouda | 1 | 500 | NTPC Ltd | CS
9 | Mouda | 2 | 500 | NTPC Ltd | CS
10 | Mouda | 3 | 660 | NTPC Ltd | CS
11 | NSPCL | 1 | 250 | NSPCL | CS
12 | NSPCL | 2 | 250 | NSPCL | CS
13 | Sipat-I | 1 | 660 | NTPC Ltd | CS
14 | Sipat-I | 2 | 660 | NTPC Ltd | CS
15 | Sipat-I | 3 | 660 | NTPC Ltd | CS
16 | Sipat-II | 4 | 500 | NTPC Ltd | CS
17 | Sipat-II | 5 | 500 | NTPC Ltd | CS
18 | SSP CBPH (Hy) | 1 | 50 | NCA | CS
19 | SSP CBPH (Hy) | 2 | 50 | NCA | CS
20 | SSP CBPH (Hy) | 3 | 50 | NCA | CS
21 | SSP CBPH (Hy) | 4 | 50 | NCA | CS
22 | SSP CBPH (Hy) | 5 | 50 | NCA | CS
23 | SSP RBPH (Hy) | 1 | 200 | NCA | CS
24 | SSP RBPH (Hy) | 2 | 200 | NCA | CS
25 | SSP RBPH (Hy) | 3 | 200 | NCA | CS
26 | SSP RBPH (Hy) | 4 | 200 | NCA | CS
27 | SSP RBPH (Hy) | 5 | 200 | NCA | CS
28 | SSP RBPH (Hy) | 6 | 200 | NCA | CS
29 | Vindhyachal-I | 1 | 210 | NTPC Ltd | CS
30 | Vindhyachal-I | 2 | 210 | NTPC Ltd | CS
31 | Vindhyachal-I | 3 | 210 | NTPC Ltd | CS
32 | Vindhyachal-I | 4 | 210 | NTPC Ltd | CS
33 | Vindhyachal-I | 5 | 210 | NTPC Ltd | CS
34 | Vindhyachal-I | 6 | 210 | NTPC Ltd | CS
35 | Vindhyachal-II | 7 | 500 | NTPC Ltd | CS
36 | Vindhyachal-II | 8 | 500 | NTPC Ltd | CS
37 | Vindhyachal-III | 9 | 500 | NTPC Ltd | CS
38 | Vindhyachal-III | 10 | 500 | NTPC Ltd | CS
39 | Vindhyachal-IV | 11 | 500 | NTPC Ltd | CS
40 | Vindhyachal-IV | 12 | 500 | NTPC Ltd | CS
41 | Vindhyachal-V | 13 | 500 | NTPC Ltd | CS
|  | Total | 13950
Private Sector
Sl. No. | Name of Station | Name of Stage/ Unit | Installed capacity (MW) | Name of Utility | Sector (CS/SS/Private)
1 | Balco | 1 | 300 | Balco | Private
2 | Balco | 2 | 300 | Balco | Private
3 | Balco | 4 | 300 | Balco | Private
4 | CGPL | 10 | 830 | Tata Power | Private
5 | CGPL | 20 | 830 | Tata Power | Private
6 | CGPL | 30 | 830 | Tata Power | Private
7 | CGPL | 40 | 830 | Tata Power | Private
8 | CGPL | 50 | 830 | Tata Power | Private
9 | DB Power | 1 | 600 | DB Power Ltd. | Private
10 | DB Power | 2 | 600 | DB Power Ltd. | Private
11 | Dhariwal | 2 | 300 | Dhariwal-Infra | Private
12 | EMCO | 1 | 300 | EMCO | Private
13 | EMCO | 2 | 300 | EMCO | Private
14 | Essar Power(Mahan) | 1 | 600 | Essar Power(Mahan) | Private
15 | GMR-CG | 1 | 685 | GMR | Private
16 | GMR-CG | 2 | 685 | GMR | Private
17 | Jhabua | 1 | 600 | Jhabua Power Ltd | Private
18 | Jindal TPP | 1 | 250 | Jindal Power | Private
19 | Jindal TPP | 2 | 250 | Jindal Power | Private
20 | Jindal TPP | 3 | 250 | Jindal Power | Private
21 | Jindal TPP | 4 | 250 | Jindal Power | Private
22 | JPL IPP | 1 | 600 | Jindal Power | Private
23 | JPL IPP | 2 | 600 | Jindal Power | Private
24 | JPL IPP | 3 | 600 | Jindal Power | Private
25 | JPL IPP | 4 | 600 | Jindal Power | Private
26 | JP-Nigrie | 1 | 660 | Jaypee | Private
27 | JP-Nigrie | 2 | 660 | Jaypee | Private
28 | KSK Mahanadi | 1 | 600 | KSK Mahanadi | Private
29 | KSK Mahanadi | 2 | 600 | KSK Mahanadi | Private
30 | KWPCL | 1 | 600 | KWPCL | Private
31 | Lanco | 1 | 300 | Lanco Amarkantak | Private
32 | Lanco | 2 | 300 | Lanco Amarkantak | Private
33 | MB-Power | 1 | 600 | Hindustan Power Ltd | Private
34 | MB-Power | 2 | 600 | Hindustan Power Ltd | Private
35 | MCCPL | 1 | 300 | ACBIL | Private
36 | RKM | 1 | 360 | RKM | Private
37 | RKM | 2 | 360 | RKM | Private
38 | Sasan_UMPP | 1 | 660 | Reliance Energy | Private
39 | Sasan_UMPP | 2 | 660 | Reliance Energy | Private
40 | Sasan_UMPP | 3 | 660 | Reliance Energy | Private
41 | Sasan_UMPP | 4 | 660 | Reliance Energy | Private
42 | Sasan_UMPP | 5 | 660 | Reliance Energy | Private
43 | Sasan_UMPP | 6 | 660 | Reliance Energy | Private
44 | TRN | 1 | 300 | TRN | Private
|  | Total | 23320

## IR
Path Details | Voltage(kV) | Link Details | Owner | No. of Circuits | Length(in circuit km)
WR-NR | 400 | HVDC Vindhyachal Back to Back (500 MW) | NRTS-1 | 2 blocks | -
| +/-500 | HVDC APL(Mundra)-Mohindargarh (2500MW)-Bipole | ATIL | Bipole | 1978
| 765 | Gwalior-Agra | NRTS-1/WRTS-2 | D/C | 258
|  | Gwalior-Jaipur | NRTS-1/WRTS-2 | D/C | 615
| 400 | Zerda-Kankroli | WRTS-2/NRTS-1 | S/C | 234
|  | Zerda-Bhinmal | WRTS-2/NRTS-1 | S/C | 143
|  | Shujalpur-RAPP | RTCL | D/C | 402
|  | Vindhyachal-IV-Rihand | WRTS-2/NRTS-1 | S/C | 60
| 220 | Badod-Kota | Madhya Pradesh / Rajasthan | S/C | 199
|  | Bhanpura-Modak | Madhya Pradesh / Rajasthan | S/C | 45
|  | Mehgaon-Auraiya | Madhya Pradesh / Uttar Pradesh | S/C | 113
|  | Malanpur-Auraiya | Madhya Pradesh / Uttar Pradesh | S/C | 146
| 132 | Neemuch-Nimbahera | Madhya Pradesh / Rajasthan | S/C | 45
|  | Seopur Kalan-Sawai Madhopur (Khandar) | Madhya Pradesh / Rajasthan | S/C | 62
|  | Gandhi Sagar-Ranapratap Sagar-I&II | Madhya Pradesh / Rajasthan | D/C | 102
|  | Bina-Morwa | Madhya Pradesh / Uttar Pradesh | S/C | 9
|  | Rajghat-Lalitpur | Madhya Pradesh / Uttar Pradesh | S/C | 23
WR-SR | 765 | Sholapur-Raichur | WRTS-1 | D/C | 416
| 400 | Bhadravati Back to Back (2x500 MW) | WRTS-1 | 2 blocks | -
|  | Bhadravati HVDC-Ramagundam | WRTS-1/SRTS-1 | D/C | 356
|  | Kholpaur-PG-Kudgi | WRTS-1/SRTS-1 | D/C | 392
| 220 | Kolhaphur(Mudshingi)-Chikkodi | MSETCL,KPTCL | S/C | 155
| 220 | Kolhaphur(Talandage)-Chikkodi | MSETCL,KPTCL | S/C | 150
|  | Ponda-Ambewadi | GED, KPTCL | S/C | 42
|  | Xeldem-Ambewadi | GED, KPTCL | S/C | 48
WR-ER | 400 | Raigarh-IBPL | WRTS-1 | S/C | 114
|  | Raigarh-Jharsuguda | WRTS-1 | S/C | 142
|  | Raigarh-Sterlite | WRTS-1 | S/C | 99
|  | Raigarh-Rourkella | WRTS-1 | S/C | 209
|  | Sipat-Ranchi | WRTS-1 | D/C | 810
| 765 | Dharamjaigarh-Ranchi | WRTS-1 | D/C | 303
|  | Dharamjaigarh-Jharsuguda | WRTS-1 | D/C | 606
| 220KV | Raigarh-Budhipadar | OPTCL/CSPTCL | S/C | 105
|  | Korba(East)-II-Budhipadar | OPTCL/CSPTCL | S/C | 176
|  | Korba(East)-III-Budhipadar | WRTS-1 | S/C | 176
D/C : Double Circuit, S/C: Single Circuit

## RGMO FGMO
NTPC
Sl. No. | Name of Station | Name of Stage/ Unit | Installed capacity (MW) | Name of Utility | Sector (CS/SS/Private)
1 | Korba STPS | 1 | 200 | NTPC Ltd | CS
2 | Korba STPS | 2 | 200 | NTPC Ltd | CS
3 | Korba STPS | 3 | 200 | NTPC Ltd | CS
4 | Korba STPS | 4 | 500 | NTPC Ltd | CS
5 | Korba STPS | 5 | 500 | NTPC Ltd | CS
6 | Korba STPS | 6 | 500 | NTPC Ltd | CS
7 | Korba STPS | 7 | 500 | NTPC Ltd | CS
8 | Mouda | 1 | 500 | NTPC Ltd | CS
9 | Mouda | 2 | 500 | NTPC Ltd | CS
10 | Sipat-I | 1 | 660 | NTPC Ltd | CS
11 | Sipat-I | 2 | 660 | NTPC Ltd | CS
12 | Sipat-I | 3 | 660 | NTPC Ltd | CS
13 | Sipat-II | 4 | 500 | NTPC Ltd | CS
14 | Sipat-II | 5 | 500 | NTPC Ltd | CS
15 | Vindhyachal-I | 1 | 210 | NTPC Ltd | CS
16 | Vindhyachal-I | 2 | 210 | NTPC Ltd | CS
17 | Vindhyachal-I | 3 | 210 | NTPC Ltd | CS
18 | Vindhyachal-I | 4 | 210 | NTPC Ltd | CS
19 | Vindhyachal-I | 5 | 210 | NTPC Ltd | CS
20 | Vindhyachal-I | 6 | 210 | NTPC Ltd | CS
21 | Vindhyachal-II | 7 | 500 | NTPC Ltd | CS
22 | Vindhyachal-II | 8 | 500 | NTPC Ltd | CS
23 | Vindhyachal-III | 9 | 500 | NTPC Ltd | CS
24 | Vindhyachal-III | 10 | 500 | NTPC Ltd | CS
25 | Vindhyachal-IV | 11 | 500 | NTPC Ltd | CS
26 | Vindhyachal-IV | 12 | 500 | NTPC Ltd | CS
27 | Vindhyachal-V | 13 | 500 | NTPC Ltd | CS
|  | Sub Total | 11340
NCA
Sl. No. | Name of Station | Name of Stage/ Unit | Installed capacity (MW) | Name of Utility | Sector (CS/SS/Private)
1 | SSP CBPH (Hy) | 1 | 50 | NCA | CS
2 | SSP CBPH (Hy) | 2 | 50 | NCA | CS
3 | SSP CBPH (Hy) | 3 | 50 | NCA | CS
4 | SSP CBPH (Hy) | 4 | 50 | NCA | CS
5 | SSP CBPH (Hy) | 5 | 50 | NCA | CS
6 | SSP RBPH (Hy) | 1 | 200 | NCA | CS
7 | SSP RBPH (Hy) | 2 | 200 | NCA | CS
8 | SSP RBPH (Hy) | 3 | 200 | NCA | CS
9 | SSP RBPH (Hy) | 4 | 200 | NCA | CS
10 | SSP RBPH (Hy) | 5 | 200 | NCA | CS
11 | SSP RBPH (Hy) | 6 | 200 | NCA | CS
|  | Sub Total | 1450
CGPL
Sl. No. | Name of Station | Name of Stage/ Unit | Installed capacity (MW) | Name of Utility | Sector (CS/SS/Private)
1 | CGPL | 10 | 830 | Tata Power | Private
2 | CGPL | 20 | 830 | Tata Power | Private
3 | CGPL | 30 | 830 | Tata Power | Private
4 | CGPL | 40 | 830 | Tata Power | Private
5 | CGPL | 50 | 830 | Tata Power | Private
|  | Sub Total | 4150
Sasan
Sl. No. | Name of Station | Name of Stage/ Unit | Installed capacity (MW) | Name of Utility | Sector (CS/SS/Private)
1 | Sasan_UMPP | 1 | 660 | Reliance Energy | Private
2 | Sasan_UMPP | 2 | 660 | Reliance Energy | Private
3 | Sasan_UMPP | 3 | 660 | Reliance Energy | Private
4 | Sasan_UMPP | 4 | 660 | Reliance Energy | Private
5 | Sasan_UMPP | 5 | 660 | Reliance Energy | Private
6 | Sasan_UMPP | 6 | 660 | Reliance Energy | Private
|  | Sub Total | 3960
Essar (Mahan)
Sl. No | Name of Station | Name of Stage/ Unit | Installed capacity (MW) | Name of Utility | Sector (CS/SS/Private)
1 | Essar Power(Mahan) | 1 | 600 | Essar Power(Mahan) | Private
KSK
Sl. No. | Name of Station | Name of Stage/ Unit | Installed capacity (MW) | Name of Utility | Sector (CS/SS/Private)
1 | KSK Mahanadi | 1 | 600 | KSK Mahanadi | Private
2 | KSK Mahanadi | 2 | 600 | KSK Mahanadi | Private
|  | Sub Total | 1200
DB-Power
Sl. No | Name of Station | Name of Stage/ Unit | Installed capacity (MW) | Name of Utility | Sector (CS/SS/Private)
1 | DB Power | 1 | 600 | DB Power Ltd. | Private
2 | DB Power | 2 | 600 | DB Power Ltd. | Private
LANCO
Sl. No | Name of Station | Name of Stage/ Unit | Installed capacity (MW) | Name of Utility | Sector (CS/SS/Private)
1 | Lanco | 1 | 300 | Lanco Amarkantak | Private
2 | Lanco | 2 | 300 | Lanco Amarkantak | Private
|  | Sub Total | 600
JPL
Sl. No | Name of Station | Name of Stage/ Unit | Installed capacity (MW) | Name of Utility | Sector (CS/SS/Private)
1 | Jindal TPP | 1 | 250 | Jindal Power | Private
2 | Jindal TPP | 2 | 250 | Jindal Power | Private
3 | Jindal TPP | 3 | 250 | Jindal Power | Private
4 | Jindal TPP | 4 | 250 | Jindal Power | Private
5 | JPL IPP | 1 | 600 | Jindal Power | Private
6 | JPL IPP | 2 | 600 | Jindal Power | Private
7 | JPL IPP | 3 | 600 | Jindal Power | Private
|  | Sub Total | 2800
JP-Nigrie
Sl. No | Name of Station | Name of Stage/ Unit | Installed capacity (MW) | Name of Utility | Sector (CS/SS/Private)
1 | JP-Nigrie | 1 | 660 | Jaypee | Private
2 | JP-Nigrie | 2 | 660 | Jaypee | Private
1320
MB Power
Sl. No | Name of Station | Name of Stage/ Unit | Installed capacity (MW) | Name of Utility | Sector (CS/SS/Private)
1 | MB-Power | 1 | 600 | Hindustan Power Ltd | Private
2 | MB-Power | 2 | 600 | Hindustan Power Ltd | Private
KWPCL
Sl. No | Name of Station | Name of Stage/ Unit | Installed capacity (MW) | Name of Utility | Sector (CS/SS/Private)
1 | KWPCL | 1 | 600 | KWPCL | Private
Dhariwal
Sl. No | Name of Station | Name of Stage/ Unit | Installed capacity (MW) | Name of Utility | Sector (CS/SS/Private)
1 | Dhariwal | 2 | 300 | Dhariwal-Infra | Private
GMR-CG
Sl. No | Name of Station | Name of Stage/ Unit | Installed capacity (MW) | Name of Utility | Sector (CS/SS/Private)
1 | GMR-CG | 1 | 685 | GMR | Private
2 | GMR-CG | 2 | 685 | GMR | Private
EMCO
Sl. No. | Name of Station | Name of Stage/ Unit | Installed capacity (MW) | Name of Uitlity | Sector (CS/SS/Private)
1 | EMCO | 1 | 300 | EMCO | Private
2 | EMCO | 2 | 300 | EMCO | Private
|  | Sub-Total | 600
Balco
Sl. No. | Name of Station | Name of Stage/ Unit | Installed capacity (MW) | Name of Uitlity | Sector (CS/SS/Private)
1 | Balco | 1 | 300 | Balco | Private
2 | Balco | 2 | 300 | Balco | Private
3 | Balco | 4 | 300 | Balco | Private
|  | Sub-Total | 900
RKM
Sl. No. | Name of Station | Name of Stage/ Unit | Installed capacity (MW) | Name of Uitlity | Sector (CS/SS/Private)
1 | RKM | 1 | 360 | RKM | Private
2 | RKM | 2 | 360 | RKM | Private
|  | Sub-Total | 720
MCCPL
Sl. No. | Name of Station | Name of Stage/ Unit | Installed capacity (MW) | Name of Uitlity | Sector (CS/SS/Private)
1 | MCCPL | 1 | 300 | ACBIL | Private

## 400 SC MVA
Sl. Nos | BUS | kV | Three Phase Fault
|  |  | Three phase fault current (kA) | Three phase fault MVA
1 | ACBIL | 400 | 14.3037 | 9909.6034
2 | Akola | 400 | 29.3256 | 20316.7757
3 | Akola(2) | 400 | 28.3432 | 19636.169
4 | Amreli | 400 | 12.9501 | 8971.8293
5 | APL-Mundra | 400 | 34.5876 | 23962.2893
6 | Asoj | 400 | 39.7567 | 27543.4418
7 | Astha | 400 | 6.4019 | 4435.2363
8 | Aurangabad-M(Waluj) | 400 | 29.7195 | 20589.6696
9 | Aurangabad-PG | 400 | 32.0889 | 22231.1899
10 | Bableshwar | 400 | 26.4524 | 18326.2227
11 | Bachau | 400 | 30.1452 | 20884.5946
12 | Balco | 400 | 23.0793 | 15989.339
13 | Bhadrawati | 400 | 41.5747 | 28802.9522
14 | Bhatapara | 400 | 14.5798 | 10100.8854
15 | Bhilai | 400 | 39.6318 | 27456.911
16 | Bhopal-BDTCL | 400 | 33.6427 | 23307.6626
17 | Bhopal-MP | 400 | 35.6076 | 24668.9453
18 | Bhusawal (Khadka) | 400 | 22.1173 | 15322.8654
19 | Bilaspur | 400 | 26.55 | 18393.84
20 | Bina-MP | 400 | 38.9035 | 26952.3448
21 | Bina-PG | 400 | 39.081 | 27075.3168
22 | Birsingpur | 400 | 18.1509 | 12574.9435
23 | Boisar | 400 | 23.7797 | 16474.5762
24 | CGPL | 400 | 29.5822 | 20494.5482
25 | Chakan | 400 | 22.2497 | 15414.5922
26 | Chandrapur | 400 | 48.2771 | 33446.3749
27 | Chandrapur-II | 400 | 47.7785 | 33100.9448
28 | Chhegaon | 400 | 8.8405 | 6124.6984
29 | Chorania | 400 | 32.3986 | 22445.7501
30 | Damoh | 400 | 12.1877 | 8443.6386
31 | DB-Power | 400 | 32.4558 | 22485.3782
32 | Deepnagar | 400 | 21.9519 | 15208.2763
33 | Dehgam | 400 | 39.1891 | 27150.2085
34 | DGEN | 400 | 12.1983 | 8450.9822
35 | Dhariwal | 400 | 31.8247 | 22048.1522
36 | Dhariwal-MS | 400 | 23.8618 | 16531.455
37 | Dhule-BDTCL | 400 | 13.1009 | 9076.3035
38 | Dhule-MS | 400 | 17.1125 | 11855.54
39 | EMCO | 400 | 25.4934 | 17661.8275
40 | Essar_Mahan | 400 | 17.0609 | 11819.7915
41 | Gandhar | 400 | 27.8422 | 19289.0762
42 | GMR-CG | 400 | 15.3233 | 10615.9822
43 | GPEC | 400 | 22.5255 | 15605.6664
44 | Gwalior | 400 | 23.7349 | 16443.5387
45 | Hadala | 400 | 18.0458 | 12502.1302
46 | Hazira | 400 | 10.0284 | 6947.6755
47 | IEPL | 400 | 14.3942 | 9972.3018
48 | Indira Sagar | 400 | 18.4351 | 12771.8373
49 | Indore-MP | 400 | 31.216 | 21626.4448
50 | Indore-PG | 400 | 29.1737 | 20211.5394
51 | Itarsi | 400 | 35.2628 | 24430.0678
52 | Jabalpur | 400 | 36.5295 | 25307.6376
53 | Jabalpur (PS) | 400 | 37.6062 | 26053.5754
54 | Jaigad | 400 | 20.0816 | 13912.5325
55 | Jejuri | 400 | 14.4099 | 9983.1787
56 | Jetpur | 400 | 12.9345 | 8961.0216
57 | Jhabua Power | 400 | 15.5877 | 10799.1586
58 | JP-Bina | 400 | 28.2148 | 19547.2134
59 | JPL | 400 | 31.0481 | 21510.1237
60 | JPL_extn(Tamnar) | 400 | 31.6435 | 21922.6168
61 | JP-Nigrie | 400 | 15.3233 | 10615.9822
62 | Julwania | 400 | 6.7784 | 4696.0755
63 | Kala | 400 | 15.3651 | 10644.9413
64 | Kalwa | 400 | 25.3932 | 17592.409
65 | Karad | 400 | 23.6934 | 16414.7875
66 | Kasor | 400 | 17.8692 | 12379.7818
67 | Katni | 400 | 6.899 | 4779.6272
68 | Khandwa | 400 | 20.3257 | 14081.645
69 | Khaparkheda | 400 | 27.1442 | 18805.5018
70 | Kharghar | 400 | 19.8329 | 13740.2331
71 | Kolhapur | 400 | 15.2053 | 10534.2318
72 | Kolhapur-PG | 400 | 11.1326 | 7712.6653
73 | Koradi | 400 | 27.9977 | 19396.8066
74 | Koradi-II | 400 | 24.89 | 17243.792
75 | Korba (W) | 400 | 33.7613 | 23389.8286
76 | Korba (W)-Ext | 400 | 32.6668 | 22631.559
77 | Korba-NTPC | 400 | 49.0375 | 33973.18
78 | Kosamba | 400 | 18.6688 | 12933.7446
79 | Koyna stage-IV | 400 | 23.7905 | 16482.0584
80 | KSK Mahanadi | 400 | 24.4475 | 16937.228
81 | KWPCL | 400 | 25.1841 | 17447.5445
82 | Lonikhand | 400 | 26.0362 | 18037.8794
83 | Lonikhand-II | 400 | 25.7624 | 17848.1907
84 | Magarawada | 400 | 26.0362 | 18037.8794
85 | Malwa | 400 | 25.7624 | 17848.1907
86 | Mansar | 400 | 14.0943 | 9764.531
87 | Mapusa | 400 | 5.8736 | 4069.2301
88 | Marwa | 400 | 12.2613 | 8494.6286
89 | MB Power | 400 | 10.5023 | 7275.9934
90 | MCCPL | 400 | 14.2971 | 9905.0309
91 | Mouda | 400 | 13.4695 | 9331.6696
92 | Nagda | 400 | 23.573 | 16331.3744
93 | Nagothane | 400 | 15.6822 | 10864.6282
94 | Nandgaonpeth | 400 | 21.5323 | 14917.5774
95 | Navsari | 400 | 19.9597 | 13828.0802
96 | New koyna | 400 | 25.3774 | 17581.4627
97 | NSPCL | 400 | 31.5805 | 21878.9704
98 | Padghe | 400 | 32.4199 | 22460.5067
99 | Parli-M | 400 | 30.3593 | 21032.923
100 | Parli-PG | 400 | 30.5895 | 21192.4056
101 | Pathadi | 400 | 20.4915 | 14196.5112
102 | Pirana-PG | 400 | 28.2065 | 19541.4632
103 | Pirana-T | 400 | 26.3223 | 18236.0894
104 | Pithampur | 400 | 18.0983 | 12538.5022
105 | Pune-PG | 400 | 29.4468 | 20400.743
106 | Pune-PG(Shikrapur) | 400 | 20.973 | 14530.0944
107 | Raigarh | 400 | 44.0702 | 30531.8346
108 | Raigarh-PS(Kotra) | 400 | 43.4028 | 30069.4598
109 | Raipur | 400 | 37.7385 | 26145.2328
110 | Raipur-PS(Durg) | 400 | 30.9447 | 21438.4882
111 | Raita | 400 | 22.579 | 15642.7312
112 | Rajgarh | 400 | 18.6991 | 12954.7365
113 | Ranchodpura | 400 | 30.8068 | 21342.951
114 | RGPPL | 400 | 14.286 | 9897.3408
115 | RKM | 400 | 22.3094 | 15455.9523
116 | Sami | 400 | 16.9296 | 11728.8269
117 | Sasan | 400 | 50.9448 | 35294.5574
118 | Satna | 400 | 37.4158 | 25921.6662
119 | Satpura | 400 | 23.8009 | 16489.2635
120 | Seoni | 400 | 32.4849 | 22505.5387
121 | Sholapur-M | 400 | 10.7715 | 7462.4952
122 | Shujalpur | 400 | 15.1021 | 10462.7349
123 | Sipat | 400 | 33.7659 | 23393.0155
124 | SKS | 400 | 27.0368 | 18731.095
125 | Soja | 400 | 22.8238 | 15812.3286
126 | Solapur-NTPC | 400 | 25.3776 | 17581.6013
127 | Solapur-PG | 400 | 29.4844 | 20426.7923
128 | SSP | 400 | 20.1051 | 13928.8133
129 | Sugen | 400 | 29.1468 | 20192.903
130 | Taptithanda | 400 | 19.7368 | 13673.655
131 | Tarapur-3&4 | 400 | 23.8892 | 16550.4378
132 | Tiroda | 400 | 23.0728 | 15984.8358
133 | TRN | 400 | 24.3869 | 16895.2443
134 | Ukai | 400 | 14.9975 | 10390.268
135 | Uno-Sugen | 400 | 27.2743 | 18895.635
136 | Vadinar | 400 | 10.3132 | 7144.985
137 | Vadodara-PS | 400 | 37.1596 | 25744.1709
138 | Vandana | 400 | 24.6744 | 17094.4243
139 | Vapi | 400 | 18.0813 | 12526.7246
140 | Varsana | 400 | 30.5527 | 21166.9106
141 | Vindhyachal | 400 | 57.382 | 39754.2496
142 | Vindhyachal-IV | 400 | 55.769 | 38636.7632
143 | Vindhyachal-PS | 400 | 51.5811 | 35735.3861
144 | Vindhyachal-V | 400 | 53.8261 | 37290.7221
145 | Wanakbori | 400 | 23.2207 | 16087.301
146 | Wardha | 400 | 53.0739 | 36769.5979
147 | Warora | 400 | 42.5941 | 29509.1925
148 | Zerda(Kansari) | 400 | 16.9616 | 11750.9965

## 500MVA ICTs
Sl. No | Sub-station | Id | MVA | Voltage Ratio | Owner
1 | Asoj | 1 | 500 | 400/220 | GETCO | G
2 | Asoj | 2 | 500 | 400/220 | GETCO | G
3 | Aurangabad | 3 | 500 | 400/220 | MSETCL
4 | Bableshwar | 3 | 500 | 400/220 | MSETCL
5 | Birsingpur | 1 | 500 | 400/220 | MPPTCL
6 | Boisar | 3 | 500 | 400/220 | WRTS-1
7 | Chorania | 1 | 500 | 400/220 | GETCO | G
8 | Chorania | 2 | 500 | 400/220 | GETCO | G
9 | Deepnagar | 1 | 500 | 400/220 | MSETCL
10 | Deepnagar | 2 | 500 | 400/220 | MSETCL
11 | Dhule | 3 | 500 | 400/220 | MSETCL
12 | Gandhar | 1 | 500 | 400/220 | NTPC | G
13 | Gandhar | 2 | 500 | 400/220 | NTPC | G
14 | Gpec | 1 | 500 | 400/220 | GETCO | G
15 | Hazira | 1 | 500 | 400/220 | ESSAR | G
16 | Hazira | 2 | 500 | 400/220 | ESSAR | G
17 | Hazira | 3 | 500 | 400/220 | ESSAR | G
18 | Jejuri | 1 | 500 | 400/220 | MSETCL
19 | Jejuri | 2 | 500 | 400/220 | MSETCL
20 | Jetpur | 4 | 500 | 400/220 | GETCO | G
21 | Kalwa | 1 | 500 | 400/220 | MSETCL
22 | Kalwa | 2 | 600 | 400/220 | MSETCL
23 | Kalwa | 3 | 500 | 400/220 | MSETCL
24 | Khaparkheda | 1 | 500 | 400/220 | MSETCL
25 | Khaparkheda | 2 | 500 | 400/220 | MSETCL
26 | Kolhapur | 3 | 500 | 400/220 | MSETCL
27 | Korba (W) | 1 | 500 | 400/220 | CSEPTCL
28 | Lonikhand-2 | 1 | 500 | 400/220 | MSETCL
29 | Lonikhand-2 | 2 | 500 | 400/220 | MSETCL
30 | Nagothane | 3 | 500 | 400/220 | MSETCL
31 | Navasari | 3 | 500 | 400/220 | WRTS-2 | G
32 | New Koyna | 2 | 500 | 400/220 | MSETCL
33 | Padghe | 4 | 600 | 400/220 | MSETCL
34 | Parli | 3 | 500 | 400/220 | MSETCL
35 | Satpura | 1 | 500 | 400/220 | MPPTCL
36 | Sholapur | 1 | 500 | 400/220 | MSETCL
37 | Sholapur | 2 | 500 | 400/220 | MSETCL
38 | Soja | 1 | 500 | 400/220 | GETCO | G
39 | Soja | 2 | 500 | 400/220 | GETCO | G
40 | Warora | 1 | 500 | 400/220 | MEGPTL
41 | Warora | 2 | 500 | 400/220 | MEGPTL
|  | Sub-Total | 20700

## New Elements
Element name
400kV APL-Versana D/C
400KV APL-Kansari S/C
400kV Versana-Kansari S/C
400kV Chandrapur 2-Parli ckt-2 LILO at Nanded S/s.(400/220kV ,500MVA 2 ICT'S)
Upgradation of BR at 400kV Bina S/s to 125MVAR.
400kV Shujalpur-RAPS D/C
400/220kV,315MVA ICT-4 at Asoj S/s.
400/220kV,315MVA ICT-4 at Ranchodpura S/s.
220kV New Karapada-Kala D/C(26.977Km)
400/132kV,ICT-4 at Pirana -T
LILO of 220kV Chitegaon-Shendra D/C at Auranagabad(PG)
220kV Nanded-Nanded D/C(22Km)
400kV Interconnection of Ukai-Kosamba and Gandhar-Navsari ckt-2
765/400kV,1500MVA ICT-2 at Champa S/s,240MVAR BR and 80 MVAR BR at 400kV Side.
63MVAR BR at 400kV Vindhyachal PS
765kV Akola-II-Ektuni ckt-2(281Km)
765/400kV ICT-2 at Ektuni(1500MVA)
400kV Ektuni-Tapthithanda ckt-2 Quad Moose(5.28Km)
JPL Tamnar-2
Essar-Bachau D/C
Pune-Aurangabad D/C LILO
Athena
SKS

## 1500MVA ICTs
Sl. No | Sub-Station | Id | MVA | Voltage Ratio | Owner
1 | Akola(2) | 1 | 1500 | 765/400 | MEGPTCL
2 | Aurangabad | 1 | 1500 | 765/400 | WRTS-1
3 | Aurangabad | 2 | 1500 | 765/400 | WRTS-1
4 | Bhopal-BDTCL | 1 | 1500 | 765/400 | BDTCL
5 | Bhopal-BDTCL | 2 | 1500 | 765/400 | BDTCL
6 | Bilaspur | 1 | 1500 | 765/400 | WRTS-1
7 | Bilaspur | 2 | 1500 | 765/400 | WRTS-1
8 | Bilaspur | 3 | 1500 | 765/400 | WRTS-1
9 | Champa | 1 | 1500 | 765/400 | WRTS-1
10 | Dharamjaygarh | 1 | 1500 | 765/400 | WRTS-2
11 | Dharamjaygarh | 2 | 1500 | 765/400 | WRTS-2
12 | Dhule-BDTCL | 1 | 1500 | 765/400 | BDTCL
13 | Dhule-BDTCL | 2 | 1500 | 765/400 | BDTCL
14 | Gwalior | 1 | 1500 | 765/400 | WRTS-2
15 | Gwalior | 2 | 1500 | 765/400 | WRTS-2
16 | Indore | 1 | 1500 | 765/400 | WRTS-2
17 | Indore | 2 | 1500 | 765/400 | WRTS-2
18 | Jabalpur-PS | 1 | 1500 | 765/400 | WRTS-2
19 | Jabalpur-PS | 2 | 1500 | 765/400 | WRTS-2
20 | Koradi-III | 1 | 1500 | 765/400 | MEGPTCL
21 | Koradi-III | 2 | 1500 | 765/400 | MEGPTCL
22 | Pune (Shikrapur) | 1 | 1500 | 765/400 | WRTS-1
23 | Pune (Shikrapur) | 2 | 1500 | 765/400 | WRTS-1
24 | Raigarh-PS(kotra) | 1 | 1500 | 765/400 | WRTS-1
25 | Raigarh-PS(kotra) | 2 | 1500 | 765/400 | WRTS-1
26 | Raigarh-PS(kotra) | 3 | 1500 | 765/400 | WRTS-1
27 | Raigarh-PS(kotra) | 4 | 1500 | 765/400 | WRTS-1
28 | Raipur-PS(Durg) | 1 | 1500 | 765/400 | WRTS-1
29 | Seoni | 1 | 1500 | 765/400 | WRTS-1
30 | Seoni | 2 | 1500 | 765/400 | WRTS-1
31 | Seoni | 3 | 1500 | 765/400 | WRTS-1
32 | Sholapur-PG | 1 | 1500 | 765/400 | WRTS-1
33 | Sholapur-PG | 2 | 1500 | 765/400 | WRTS-1
34 | Tamnar-PS | 1 | 1500 | 765/400 | WRTS-1
35 | Tamnar-PS | 2 | 1500 | 765/400 | WRTS-1
36 | Tamnar-PS | 3 | 1500 | 765/400 | WRTS-1
37 | Tiroda | 1 | 1500 | 765/400 | APML
38 | Vadodara-PS | 1 | 1500 | 765/400 | WRTS-2
39 | Vadodara-PS | 2 | 1500 | 765/400 | WRTS-2
40 | Vindhyachal-PS | 1 | 1500 | 765/400 | WRTS-2
41 | Vindhyachal-PS | 2 | 1500 | 765/400 | WRTS-2
42 | Wardha | 1 | 1500 | 765/400 | WRTS-1
43 | Wardha | 2 | 1500 | 765/400 | WRTS-1
44 | Wardha | 3 | 1500 | 765/400 | WRTS-1
|  | Sub-Total | 66000

## 1000MVA ICTs
Sl No | Sub-station | From Bus Voltage | To Bus Name | To Bus Voltage | Id | MVA | Voltage Ratio | Owner
1 | BINA-PG | 400 | BINA-PG | 765 | 1 | 1000 | 765/400 | WRTS-2
2 | BINA-PG | 400 | BINA-PG | 765 | 2 | 1000 | 765/400 | WRTS-2
3 | Sasan | 400 | SASAN | 765 | 1 | 1000 | 765/400 | Reliance
4 | Sasan | 400 | SASAN | 765 | 2 | 1000 | 765/400 | Reliance
5 | Satna | 400 | SATNA | 765 | 1 | 1000 | 765/400 | WRTS-2
6 | Satna | 400 | SATNA | 765 | 2 | 1000 | 765/400 | WRTS-2
7 | Sipat | 400 | SIPAT | 765 | 1 | 1000 | 765/400 | NTPC
8 | Sipat | 400 | SIPAT | 765 | 2 | 1000 | 765/400 | NTPC
[5 empty] | Sub-total | 8000

## MP
400 kV Lines
Sl No | End-1 | End-2 | Id | Line Owner | End-1 Owner | End-2 Owner | Length(in Km) | Conductor Type
1 | Bhopal | Bina-MP | 1 | MPPTCL | MPPTCL | MPPTCL | 289 | Twin ACSR Moose
2 | Bhopal | Bina-MP | 2 | MPPTCL | MPPTCL | MPPTCL | 273 | Twin ACSR Moose
3 | Bhopal | Itarsi | 1 | MPPTCL | MPPTCL | WRST-2 | 98 | Twin ACSR Moose
4 | Bhopal | Itarsi | 2 | MPPTCL | MPPTCL | WRST-2 | 98 | Twin ACSR Moose
5 | Bina-MP | JP-Bina | 1 | MPPTCL | MPPTCL | Jaypee | 20 | Twin ACSR Moose
6 | Birsingpur | Katni | 1 | MPPTCL | MPPTCL | MPPTCL | 118 | Twin ACSR Moose
7 | Birsingpur | Katni | 2 | MPPTCL | MPPTCL | MPPTCL | 118 | Twin ACSR Moose
8 | Chhegaon | Julwania | 1 | MPPTCL | MPPTCL | MPPTCL | 114 | Twin ACSR Moose
9 | Damoh | Katni | 1 | MPPTCL | WRTS-2 | MPPTCL | 118 | Twin ACSR Moose
10 | Indira Sagar | Indore-MP | 1 | MPPTCL | MPPTCL | MPPTCL | 79 | Quad ACSR Moose
11 | Indira Sagar | Indore-MP | 2 | MPPTCL | MPPTCL | MPPTCL | 80 | Quad ACSR Moose
12 | Indira Sagar | Nagda | 1 | MPPTCL | MPPTCL | MPPTCL | 188 | Twin ACSR Moose
13 | Indore-MP | Nagda | 1 | MPPTCL | MPPTCL | MPPTCL | 108 | Twin ACSR Moose
14 | Indore-MP | Pithampur | 1 | MPPTCL | MPPTCL | MPPTCL | 150 | Twin ACSR Moose
15 | Indore-MP | Pithampur | 2 | MPPTCL | MPPTCL | MPPTCL | 150 | Twin ACSR Moose
16 | Malwa | Chhegaon | 1 | MPPTCL | MPPTCL | MPPTCL | 53 | Twin ACSR Moose
17 | Malwa | Pithampur | 1 | MPPTCL | MPPTCL | MPPTCL | 136 | Twin ACSR Moose
18 | Malwa | Pithampur | 2 | MPPTCL | MPPTCL | MPPTCL | 136 | Twin ACSR Moose
19 | Nagda | Indira Sagar | 1 | MPPTCL | MPPTCL | MPPTCL | 103 | Twin ACSR Moose
20 | Satpura | Indira-sagar | 1 | MPPTCL | MPPTCL | MPPTCL | 189 | Twin ACSR Moose
21 | Satpura | Astha | 1 | MPPTCL | MPPTCL | MPPTCL | 240 | Twin ACSR Moose
22 | SSP | Rajgarh | 1 | MPPTCL | SSNNL | MPPTCL | 178 | Twin ACSR Moose
23 | SSP | Rajgarh | 2 | MPPTCL | SSNNL | MPPTCL | 178 | Twin ACSR Moose
[6 empty] | Total | 3214
Important 220 kV Lines in MP
S.No | End-1 | End-2 | Id | Line Owner | End-1 Owner | End-2 Owner | Length(in Km) | Conductor Type
1 | Anuppur | Kotmikala | 1 | MPPTCL | CSPTCL | MPPTCL | 61 | Single Zebra
2 | Anuppur | Kotmikala | 2 | MPPTCL | CSPTCL | MPPTCL | 61 | Single Zebra
3 | Auraiya | Malanpur | 1 | MPPTCL | UPPTCL | MPPTCL | 146 | Single Zebra
4 | Auraiya | Mehgaon | 1 | MPPTCL | UPPTCL | MPPTCL | 113 | Single Zebra
5 | Badod | Sakatpur | 1 | MPPTCL | MPPTCL | RSPTCL | 199 | Single Zebra
6 | Badod | Modak | 1 | MPPTCL | MPPTCL | RSPTCL | 151 | Single Zebra
7 | Bina-MP | Bina-PG | 1 | MPPTCL | MPPTCL | WRTS-2 | 3 | Single Zebra
8 | Bina-MP | Shivpuri | 1 | MPPTCL | MPPTCL | MPPTCL | 169 | Single Zebra
9 | Bina-MP | Mahalgaon | 1 | MPPTCL | MPPTCL | MPPTCL | 246 | Single Zebra
10 | Bina-MP | Mahalgaon | 2 | MPPTCL | MPPTCL | MPPTCL | 246 | Single Zebra
11 | Damoh-MP | Damoh-PG | 1 | MPPTCL | MPPTCL | WRTS-2 | 8 | Single Zebra
12 | Damoh-MP | Damoh-PG | 2 | MPPTCL | MPPTCL | WRTS-2 | 9 | Single Zebra
13 | Damoh-PG | Sagar | 2 | MPPTCL | WRTS-2 | MPPTCL | 62 | Single Zebra
14 | Damoh-PG | Tikamgad | 1 | MPPTCL | WRTS-2 | MPPTCL | 151 | Single Zebra
15 | Gwalior | Malanpur | 1 | MPPTCL | WRTS-2 | MPPTCL | 38 | Single Zebra
16 | Gwalior | Malanpur | 2 | MPPTCL | WRTS-2 | MPPTCL | 38 | Single Zebra
17 | Gwalior | Mahalgaon | 1 | MPPTCL | WRTS-2 | MPPTCL | 11 | Single Zebra
18 | Gwalior | Mahalgaon | 2 | MPPTCL | WRTS-2 | MPPTCL | 11 | Single Zebra
19 | Hoshangabad | Itarsi-PG | 1 | MPPTCL | MPPTCL | WRTS-2 | 21 | Single Zebra
20 | Itarsi | Itarsi-PG | 1 | MPPTCL | MPPTCL | WRTS-2 | 3 | Single Zebra
21 | Jabalpur | Jabalpur-PG | 1 | MPPTCL | MPPTCL | WRTS-2 | 11 | Single Zebra
22 | Jabalpur | Jabalpur-PG | 2 | MPPTCL | MPPTCL | WRTS-2 | 11 | Single Zebra
23 | Katni | Satna-PG | 1 | MPPTCL | MPPTCL | WRTS-2 | 102 | Single Zebra
24 | Khandwa | Omkareswar | 1 | MPPTCL | WRTS-2 | MPPTCL | 98 | Single Zebra
25 | Mehgaon | Malanpur | 1 | MPPTCL | MPPTCL | MPPTCL | 37 | Single Zebra
26 | Pandurna | Kalmeshwar | 1 | MSETCL/MPPTCL | MPPTCL | MSETCL | 68 | Single Zebra
27 | Pithampura | Rajgarh-PG | 1 | MPPTCL | MPPTCL | WRTS-1 | 79 | Single Zebra
28 | Pithampura | Rajgarh-PG | 2 | MPPTCL | MPPTCL | WRTS-1 | 78 | Single Zebra
29 | Rajgarh-PG | Rajgarh-MP | 1 | MPPTCL | WRTS-2 | MPPTCL | 13 | Single Zebra
30 | Rajgarh-PG | Rajgarh-MP | 2 | MPPTCL | WRTS-2 | MPPTCL | 12 | Single Zebra
31 | Satna-MP | Satna-PG | 1 | MPPTCL | MPPTCL | WRTS-2 | 1 | Single Zebra
32 | Satna-MP | Satna-PG | 2 | MPPTCL | MPPTCL | WRTS-2 | 1 | Single Zebra
33 | Satna-PG | Maihar | 2 | MPPTCL | WRTS-2 | MPPTCL | 42 | Single Zebra
34 | Seoni-PG | Seoni-MP | 1 | MPPTCL | WRTS-1 | MPPTCL | 4 | Single Zebra
35 | Seoni-PG | Seoni-MP | 2 | MPPTCL | WRTS-1 | MPPTCL | 4 | Single Zebra
36 | Seoni-PG | Chindwara | 1 | MPPTCL | WRTS-1 | MPPTCL | 67 | Single Zebra
37 | Seoni-PG | Chindwara | 2 | MPPTCL | WRTS-1 | MPPTCL | 67 | Single Zebra
[6 empty] | Total | 2442
400/220 kV ICTs
S.No | Sub-station | Id | MVA | Voltage Ratio | Owner
1 | Birsingpur | 1 | 500 | 400/220 | MPPTCL
2 | Satpura | 1 | 500 | 400/220 | MPPTCL
3 | Astha | 1 | 315 | 400/220 | MPPTCL
4 | Astha | 2 | 315 | 400/220 | MPPTCL
5 | Bhopal | 1 | 315 | 400/220 | MPPTCL
6 | Bhopal | 2 | 315 | 400/220 | MPPTCL
7 | Bhopal | 3 | 315 | 400/220 | MPPTCL
8 | Bina | 1 | 315 | 400/220 | MPPTCL
9 | Bina | 2 | 315 | 400/220 | MPPTCL
10 | Bina | 3 | 315 | 400/220 | MPPTCL
11 | Chegaon | 1 | 315 | 400/220 | MPPTCL
12 | Indore | 1 | 315 | 400/220 | MPPTCL
13 | Indore | 2 | 315 | 400/220 | MPPTCL
14 | Indore | 3 | 315 | 400/220 | MPPTCL
15 | Indore | 4 | 315 | 400/220 | MPPTCL
16 | Katni | 1 | 315 | 400/220 | MPPTCL
17 | Malwa | 1 | 315 | 400/220 | MPPTCL
18 | Nagda | 1 | 315 | 400/220 | MPPTCL
19 | Nagda | 2 | 315 | 400/220 | MPPTCL
20 | Nagda | 3 | 315 | 400/220 | MPPTCL
21 | Pithampur | 1 | 315 | 400/220 | MPPTCL
22 | Pithampur | 2 | 315 | 400/220 | MPPTCL
|  | Total | 7300
BRs at 400kV Substations
S.No | Name of S/S | Owner | Nos of Reactor | Total MVAR | Rated Voltage
1 | Bhopal | MPPTCL | 1X125 | 125 | 420
2 | Bina(MP) | MPPTCL | 1X50 | 50 | 420
3 | Birsinghpur | MPPTCL | 1X50 | 50 | 420
4 | Nagda | MPPTCL | 2X50 | 100 | 420
5 | Nagda | MPPTCL | 2X50 | 100 | 420
6 | Satpura | MPPTCL | 2X63 | 126 | 420
|  |  | Total | 551
LRs at 400kV Substations
Sr. No. | Name of the Line | Reactor capacity in MVAR
|  | End 1 |  | End 2
1 | Satpura-Seoni-S/C | - |  | 50
2 | Bhopal-Bina-1 | - |  | 50
3 | Bhopal-Bina-2 | - |  | 50
4 | Indore-Indirasagar-2 | 50 |  | -
5 | Damoh-Birsighpur-S/C | 50 |  | -
6 | Indore-Itarasi-1 | 50 |  | -
7 | Indore-Itarasi-2 | 50 |  | -
8 | Indore-Asoj-1 | 50 |  | -
9 | Nagda-Rajgarh-1 | 50 |  | -
10 | Nagda-Rajgarh-2 | 50 |  | -
11 | Nagda-Bina-1 | 63 |  | -
12 | Nagda-Bina-2 | 63 |  | -
13 | Nagda-Dehgam-1 | 50 |  | -
14 | Nagda-Dehgam-2 | 50 |  | -
| TOTAL | 576 |  | 150

## 315MVA ICTs
Sl No | Sub-station | Id | MVA | Voltage Ratio | Owner
1 | Akola | 1 | 315 | 400/220 | MSETCL
2 | Akola | 2 | 315 | 400/220 | MSETCL
3 | Amreli | 1 | 315 | 400/220 | GETCO | G
4 | Amreli | 2 | 315 | 400/220 | GETCO | G
5 | Amreli | 3 | 315 | 400/220 | GETCO | G
6 | Astha | 1 | 315 | 400/220 | MPPTCL
7 | Astha | 2 | 315 | 400/220 | MPPTCL
8 | Asoj | 3 | 315 | 400/220 | GETCO | G
9 | Aurangabad | 1 | 315 | 400/220 | MSETCL
10 | Aurangabad | 2 | 315 | 400/220 | MSETCL
11 | Aurangabad-PG | 1 | 315 | 400/220 | WRTS-1
12 | Aurangabad-PG | 2 | 315 | 400/220 | WRTS-1
13 | Bableshwar | 1 | 315 | 400/220 | MSETCL
14 | Bableshwar | 2 | 315 | 400/220 | MSETCL
15 | Bachau | 1 | 315 | 400/220 | WRTS-2 | G
16 | Bachau | 2 | 315 | 400/220 | WRTS-2 | G
17 | Balco | 1 | 315 | 400/220 | BALCO
18 | Balco | 2 | 315 | 400/220 | BALCO
19 | Balco | 3 | 315 | 400/220 | BALCO
20 | Bhadrawathi | 1 | 315 | 400/220 | WRTS-1
21 | Bhatapara | 1 | 315 | 400/220 | WRTS-1
22 | Bhatapara | 2 | 315 | 400/220 | WRTS-1
23 | Bhilai | 1 | 315 | 400/220 | WRTS-1
24 | Bhilai | 2 | 315 | 400/220 | WRTS-1
25 | Bhilai | 3 | 315 | 400/220 | WRTS-1
26 | Bhopal | 1 | 315 | 400/220 | MPPTCL
27 | Bhopal | 2 | 315 | 400/220 | MPPTCL
28 | Bhopal | 3 | 315 | 400/220 | MPPTCL
29 | Bhusawal | 1 | 315 | 400/220 | MSETCL
30 | Bina | 1 | 315 | 400/220 | MPPTCL
31 | Bina | 2 | 315 | 400/220 | MPPTCL
32 | Bina | 3 | 315 | 400/220 | MPPTCL
33 | Bina-PG | 1 | 315 | 400/220 | WRTS-2
34 | Boisar-PG | 1 | 315 | 400/220 | WRTS-2
35 | Boisar-PG | 2 | 315 | 400/220 | WRTS-2
36 | Carnac | 1 | 315 | 220/100 | MSETCL
37 | Carn-GIS | 1 | 315 | 220/100 | MSETCL
38 | Chakan | 1 | 315 | 400/220 | MSETCL
39 | Chakan | 2 | 315 | 400/220 | MSETCL
40 | Chandrapur | 1 | 315 | 400/220 | MSETCL
41 | Chandrapur | 2 | 315 | 400/220 | MSETCL
42 | Chegaon | 1 | 315 | 400/220 | MPPTCL
43 | Damoh | 1 | 315 | 400/220 | WRTS-2
44 | Damoh | 2 | 315 | 400/220 | WRTS-2
45 | Dehgam | 1 | 315 | 400/220 | WRTS-2 | G
46 | Dehgam | 2 | 315 | 400/220 | WRTS-2 | G
47 | Dhule | 1 | 315 | 400/220 | MSETCL
48 | Dhule | 2 | 315 | 400/220 | MSETCL
49 | Gwalior | 1 | 315 | 400/220 | WRTS-2
50 | Gwalior | 2 | 315 | 400/220 | WRTS-2
51 | Gwalior | 3 | 315 | 400/220 | WRTS-2
52 | Hadala | 1 | 315 | 400/220 | GETCO | G
53 | Hadala | 2 | 315 | 400/220 | GETCO | G
54 | Hadala | 3 | 315 | 400/220 | GETCO | G
55 | Indore | 1 | 315 | 400/220 | MPPTCL
56 | Indore | 2 | 315 | 400/220 | MPPTCL
57 | Indore | 3 | 315 | 400/220 | MPPTCL
58 | Indore | 4 | 315 | 400/220 | MPPTCL
59 | Itarsi | 1 | 315 | 400/220 | WRTS-2
60 | Jabalpur | 1 | 315 | 400/220 | WRTS-2
61 | Jabalpur | 2 | 315 | 400/220 | WRTS-2
62 | Jetpur | 1 | 315 | 400/220 | GETCO | G
63 | Jetpur | 2 | 315 | 400/220 | GETCO | G
64 | Jetpur | 3 | 315 | 400/220 | GETCO | G
65 | Jindal | 1 | 315 | 400/220 | JPL
66 | Jindal | 2 | 315 | 400/220 | JPL
| Kala | 1 | 315 | 400/220 | WRTS(II)
| Kala | 2 | 315 | 400/220 | WRTS(II)
67 | Karad | 1 | 315 | 400/220 | MSETCL
68 | Karad | 2 | 315 | 400/220 | MSETCL
69 | Karad | 3 | 315 | 400/220 | MSETCL
70 | Kasor | 1 | 315 | 400/220 | GETCO | G
71 | Kasor | 2 | 315 | 400/220 | GETCO | G
72 | Katni | 1 | 315 | 400/220 | MPPTCL | G
73 | Khandwa | 1 | 315 | 400/220 | WRTS-2
74 | Khandwa | 2 | 315 | 400/220 | WRTS-2
75 | Kharghar | 1 | 315 | 400/220 | MSETCL
76 | Kharghar | 2 | 315 | 400/220 | MSETCL
77 | Kolhapur | 1 | 315 | 400/220 | MSETCL
78 | Kolhapur | 2 | 315 | 400/220 | MSETCL
79 | Koradi | 1 | 315 | 400/220 | MSETCL
80 | Koradi | 2 | 315 | 400/220 | MSETCL
81 | Kosamba | 1 | 315 | 400/220 | GETCO | G
82 | Kosamba | 2 | 315 | 400/220 | GETCO | G
83 | Lonikhand | 1 | 315 | 400/220 | MSETCL
84 | Lonikhand | 2 | 315 | 400/220 | MSETCL
85 | Lonikhand | 3 | 315 | 400/220 | MSETCL
86 | Magarwada | 1 | 315 | 400/220 | WRTS-1 | G
87 | Magarwada | 2 | 315 | 400/220 | WRTS-1 | G
88 | Malwa | 1 | 315 | 400/220 | MPPTCL
89 | Mansar | 1 | 315 | 400/220 | GETCO | G
90 | Mansar | 2 | 315 | 400/220 | GETCO | G
91 | Mapusa | 1 | 315 | 400/220 | WRTS-1
92 | Mapusa | 2 | 315 | 400/220 | WRTS-1
93 | Mapusa | 3 | 315 | 400/220 | WRTS-1
94 | Marwa | 1 | 315 | 400/220 | CSPTCL
95 | Mundra | 1 | 315 | 400/220 | APL | G
96 | Mundra | 2 | 315 | 400/220 | APL | G
97 | Nagda | 1 | 315 | 400/220 | MPPTCL
98 | Nagda | 2 | 315 | 400/220 | MPPTCL
99 | Nagda | 3 | 315 | 400/220 | MPPTCL
100 | Nagothane | 1 | 315 | 400/220 | MSETCL
101 | Nagothane | 2 | 315 | 400/220 | MSETCL
102 | Navsari | 1 | 315 | 400/220 | WRTS-2 | G
103 | Navsari | 2 | 315 | 400/220 | WRTS-2 | G
104 | New Koyna | 1 | 315 | 400/220 | MSETCL
105 | NSPCL | 1 | 315 | 400/220 | NSPCL
106 | NSPCL | 2 | 315 | 400/220 | NSPCL
107 | Padghe | 1 | 315 | 400/220 | WRTS-2
108 | Padghe | 2 | 315 | 400/220 | WRTS-2
109 | Padghe | 3 | 315 | 400/220 | WRTS-2
110 | Parli | 1 | 315 | 400/220 | WRTS-1
111 | Parli | 2 | 315 | 400/220 | WRTS-1
112 | Pirana(T) | 1 | 315 | 400/132 | TPL | G
113 | Pirana(T) | 2 | 315 | 400/132 | TPL | G
114 | Pirana-PG | 1 | 315 | 400/220 | WRTS-2 | G
115 | Pirana-PG | 2 | 315 | 400/220 | WRTS-2 | G
116 | Pithampur | 1 | 315 | 400/220 | MPPTCL
117 | Pithampur | 2 | 315 | 400/220 | MPPTCL
118 | Pune-PG | 1 | 315 | 400/220 | WRTS-1
119 | Pune-PG | 2 | 315 | 400/220 | WRTS-1
120 | Pune-PG | 3 | 315 | 400/220 | WRTS-1
121 | Raigarh | 1 | 315 | 400/220 | WRTS-2
122 | Raigarh | 2 | 315 | 400/220 | WRTS-2
123 | Raipur | 1 | 315 | 400/220 | WRTS-1
124 | Raipur | 2 | 315 | 400/220 | WRTS-1
125 | Raipur | 3 | 315 | 400/220 | WRTS-1
126 | Raita | 1 | 315 | 400/220 | CSPTCL
127 | Raita | 2 | 315 | 400/220 | CSPTCL
128 | Rajgarh | 1 | 315 | 400/220 | WRTS-2
129 | Rajgarh | 2 | 315 | 400/220 | WRTS-2
130 | Ranchodpura | 1 | 315 | 400/220 | GETCO | G
131 | Ranchodpura | 2 | 315 | 400/220 | GETCO | G
132 | Ranchodpura | 3 | 315 | 400/220 | GETCO | G
133 | Satna-PG | 1 | 315 | 400/220 | WRTS-2
134 | Satna-PG | 2 | 315 | 400/220 | WRTS-2
135 | Seoni | 1 | 315 | 400/220 | WRTS-1
136 | Seoni | 2 | 315 | 400/220 | WRTS-1
137 | Sholapur-PG | 1 | 315 | 400/220 | WRTS-1
138 | Sholapur-PG | 2 | 315 | 400/220 | WRTS-1
139 | Shujalpur | 1 | 315 | 400/220 | WRTS-2
140 | Shujalpur | 2 | 315 | 400/220 | WRTS-2
141 | SSP | 1 | 315 | 400/220 | SSNL | G
142 | SSP | 2 | 315 | 400/220 | SSNL | G
143 | Sugen | 1 | 315 | 400/220 | TPL | G
144 | Sugen | 2 | 315 | 400/220 | TPL | G
145 | Sugen | 3 | 315 | 400/220 | TPL | G
146 | Ukai | 1 | 315 | 400/220 | GETCO | G
147 | Vapi | 1 | 315 | 400/220 | WRTS-2 | G
148 | Vapi | 2 | 315 | 400/220 | WRTS-2 | G
149 | Vapi | 3 | 315 | 400/220 | WRTS-2 | G
150 | Versana | 1 | 315 | 400/220 | GETCO | G
151 | Versana | 2 | 315 | 400/220 | GETCO | G
152 | Wanakbori | 1 | 315 | 400/220 | GETCO | G
153 | Wardha | 1 | 315 | 400/220 | WRTS-1
154 | Wardha | 2 | 315 | 400/220 | WRTS-1
155 | Zerda | 1 | 315 | 400/220 | GETCO | G
156 | Zerda | 2 | 315 | 400/220 | GETCO | G
157 | Zerda | 3 | 315 | 400/220 | GETCO | G
|  | Sub-Total | 50085

## FSC
Fixed Series Compensators (FSC)
S.N | Line Details | kV | Len (km) | FSC Location( %) | Compensation | Agency |  | Comments
1 | Seoni-Khandwa-1 | 400 | 350 | Khandwa | 40% | WRTS-2
2 | Seoni-Khandwa-2 | 400 | 350 | Khandwa | 40% | WRTS-2
3 | Rajgarh-Kasor-1 | 400 | 232 | Rajgarh | 25% | WRTS-2
4 | Rajgarh-Kasor-2 | 400 | 232 | Rajgarh | 25% | WRTS-2
5 | Raigarh-KSK-RKM-Raipur-3 | 400 | 220 | Raipur | 40% | WRTS-1 |  | Out of service since 28.7.13
6 | Raigarh-KSK-Raipur-4 | 400 | 220 | Raipur | 40% | WRTS-1 |  | Out of service since 24.7.13
7 | Adani-Sami-1 | 400 | 434 | Sami | 40% | APL
8 | Adani-Sami-2 | 400 | 434 | Sami | 40% | APL
9 | Raipur-Wardha-1 | 400 | 371 | Wardha | 40% | WRTS-1
10 | Raipur-Wardha-2 | 400 | 371 | Wardha | 40% | WRTS-1
B. Thyristor Controlled Series Capacitor (TCSC)
S.N | Line Detail | kV | Len ( km) | Location | Fixed, Variable |  | Agency
1 | Raipur-Raigarh-I | 400 | 217 | Raipur | 40% Fix, +15% / -5% Dynamic |  | WRTS-1
2 | Raipur-Raigarh-II | 400 | 217 | Raipur | 40% Fix, +15% / -5% Dynamic |  | WRTS-1 |  | Out of service since 11.04.2015